## Contingency Actions List

(For TMT review 1/19/2022)

When routine reliability tools and preemptive actions are insufficient or unavailable to resolve the power system condition, the following is a list of contingency actions that may be taken to provide reserves, voltage, energy or inertia. The order and extent of the actual implementation of the actions in this list will be dictated by each specific condition but if possible the order at each individual dam will be followed. The actions on the list may be updated as necessary through coordination with TMT.

Contingency Actions are prioritized by tier and within each tier.

| March 1 – April 2 | April 3 – April 9 | April 10 – June 15 | June 15 – June 20 | June 21 – August 14 | August 15 to August 31 | September – November 15 | November 16 - End of Feb |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Tier 1 | Tier 1 | Tier 1 | Tier 1 | Tier 1 | Tier 1 | Tier 1 | Tier 1 |
| JDA shutoff adult attraction flow | JDA shutoff adult attraction flow | Generate above 1% up to full load in the following order if possible: | Generate above 1% up to full load in the following order if possible: | Generate above 1% up to full load in the following order if possible: | Generate above 1% up to full load in the following order if possible: | TDA shut off sluiceway | TDA shut off sluiceway |
| TDA shut off sluiceway | TDA shut off sluiceway | BON | BON | BON | BON | BON shut off sluiceway | BON shut off sluiceway |
| BON shutoff adult attraction flow | BON shutoff adult attraction flow | JDA | JDA | JDA | JDA | HGH & LIB modify ramping rates | HGH, LIB, DWR, ALF, GCL: increase project drafts |
| BON shut off sluiceway | BON shut off sluiceway | TDA | TDA | TDA | TDA | HGH, LIB, DWR, ALF, GCL: increase project drafts | HGH & LIB modify ramping rates |
| BON shut of Corner Collector | BON shut of Corner Collector | MCN (up to 14.4 kcfs/unit) | MCN (up to 14.4 kcfs/unit) | MCN (up to 14.4 kcfs/unit) | MCN (up to 14.4 kcfs/unit) |  |  |
| HGH & LIB modify ramping rates | HGH & LIB modify ramping rates | IHR | IHR | IHR | IHR |  |  |
| HGH, LIB, DWR, ALF, GCL: increase project drafts | HGH, LIB, DWR, ALF, GCL: increase project drafts | LMN | LMN | LMN | LMN |  |  |
|  |  | LGS | LGS | LGS | LGS |  |  |
|  |  | LWG | LWG | LWG | LWG |  |  |
|  |  | Allow MOP excursion up to: 2 feet at IHR, LMN, LGS, and LWG | Allow MOP excursion up to: 2 feet at IHR, LMN, LGS, and LWG | Allow MOP excursion up to: 2 feet at IHR, LMN, LGS, and LWG | Allow MOP excursion up to: 2 feet at IHR, LMN, LGS, and LWG |  |  |

| March 1 – April 2 | April 3 – April 9 | April 10 – June 15 | June 15 – June 20 | June 21 – August 14 | August 15 to August 31 | September – November 15 | November 16 - End of Feb |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Tier 2 | Tier 2 | Tier 2 | Tier 2 | Tier 2 | Tier 2 | Tier 2 | Tier 2 |
| LWG Move Spillway Weir Hours | IHR 30% of flow | LWG 20 kcfs | LWG 20 kcfs | LWG Spillway Weir | - Reduce spill to zero | LWG Move Spillway Weir Hours |  |
| LGS Move Spillway Weir Hours | LMN 30 kcfs flat | LGS 30% of flow | LGS 30% of flow | LGS Spillway Weir | LWG | LGS Move Spillway Weir Hours |  |
| LMN Move Spillway Weir Hours | LGS 30% of flow | IHR 30% of flow | IHR 30% of flow | IHR Spillway Weir | LGS | LMN Move Spillway Weir Hours |  |
| IHR Move Spillway Weir Hours | LWG 20 kcfs | MCN 40% of flow | MCN 40% of flow | MCN 40% of flow | LMN | IHR Move Spillway Weir Hours |  |
| MCN Move Spillway Weir Hours |  | JDA 30% of flow | JDA 30% of flow | JDA 30% of flow | IHR | MCN Move Spillway Weir Hours |  |
| JDA Move Spillway Weir Hours |  | TDA 30% of flow | TDA 30% of flow | TDA 30% of flow | MCN | JDA Move Spillway Weir Hours |  |
|  |  | BON 100 kcfs | BON 100 kcfs | BON 75 kcfs | JDA |  |  |
|  |  | MCN generate outside 1% up to full load | MCN generate outside 1% up to full load | MCN generate outside 1% up to full load |  |  |  |
|  |  | BON2 operate outside 1% up to full load | BON2 operate outside 1% up to full load | BON2 operate outside 1% up to full load |  |  |  |
|  |  | Allow MOP excursion up to 3 feet at IHR, LMN, LGS, and LWG | Allow MOP excursion up to 3 feet at IHR, LMN, LGS, and LWG | Allow MOP excursion up to 3 feet at IHR, LMN, LGS, and LWG |  |  |  |
| Tier 3 | Tier 3 | Tier 3 | Tier 3 | Tier 3 | Tier 3 | Tier 3 | Tier 3 |
|  | – Reduce Spill to Spillway weir(s) only | LWG 18 kcfs of spill | LWG 18 kcfs of spill | MCN 30% of flow |  | Curtail Spillway Weir spill |  |
|  | LWG 7 kcfs | LMN 30% of flow | LMN 30% of flow | JDA Spillway Weir only |  | LWG |  |
|  | LGS 7 kcfs | MCN 30% of flow | MCN 30% of flow | – Reduce Spill to zero |  | LGS |  |
|  | LMN 7 kcfs | TDA 30% of flow | TDA 30% of flow | IHR |  | LMN |  |
|  | IHR 7 kcfs | BON 95 kcfs | BON 95 kcfs | LMN |  | IHR |  |
|  | TDA 20% of flow |  |  | LGS |  | MCN |  |
|  | BON 75 kcfs |  |  | LWG |  | JDA |  |
| Tier 4 | Tier 4 | Tier 4 | Tier 4 | Tier 4 | Tier 4 | Tier 4 | Tier 4 |
|  | BON 50 kcfs | – Reduce Spill to Spillway weir(s) only | – Reduce Spill to Spillway weir(s) only | BON 50 kcfs |  |  |  |
|  |  | LWG 7 kcfs | LWG 7 kcfs |  |  |  |  |
|  |  | LGS 7 kcfs | LGS 7 kcfs |  |  |  |  |
|  |  | LMN 7 kcfs | LMN 7 kcfs |  |  |  |  |
|  |  | IHR 7 kcfs | IHR 7 kcfs |  |  |  |  |
|  |  | TDA 20% of flow | TDA 20% of flow |  |  |  |  |
|  |  | BON 75 kcfs | BON 75 kcfs |  |  |  |  |

| March 1 – April 2 | April 3 – April 9 | April 10 – June 15 | June 15 – June 20 | June 21 – August 14 | August 15 to August 31 | September – November 15 | November 16 - End of Feb |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Tier 5 | Tier 5 | Tier 5 | Tier 5 | Tier 5 | Tier 5 | Tier 5 |  | Tier 5 |
|  | BON to zero | 50 kcfs at BON |  |  |  |  |  |  |
| Tier 6 | Tier 6 | Tier 6 | Tier 6 | Tier 6 | Tier 6 | Tier 6 | Tier 6 |  |
|  | - Reduce spill to zero | - Reduce spill to zero |  |  |  |  |  |  |
|  | LWG | LWG |  |  |  |  |  |  |
|  | LGS | LGS |  |  |  |  |  |  |
|  | LMN | LMN |  |  |  |  |  |  |
|  | IHR | IHR |  |  |  |  |  |  |
|  | MCN | MCN |  |  |  |  |  |  |
|  | JDA | JDA |  |  |  |  |  |  |
|  | TDA | TDA |  |  |  |  |  |  |