# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	18ALL001 – Add Operating Limit Limits to 1% Tables

Date Submitted: 		February 1, 2018

Project: 			All Projects (BON, TDA, JDA, MCN, IHR, LMN, LGS, LWG)

Requester Name, Agency: 	Scott Bettin, BPA

Final Action:			APPROVED as Revised 2/8/18

FPP Section:

All project turbine 1% efficiency range tables.

Justification for Change:

- Add columns to the turbine 1% tables to define Power (MW) and Flow (cfs) at the turbine “Operating Limit” (maximum operating point based on the cavitation limit or generator limit).

- Update footnotes where necessary to reflect current status of all fixed-blade units and other limitations.

Proposed Change:

See following pages for revised turbine 1% efficiency tables for all projects (new text in red).

Comments:

2/8/18 FPOM: This was a new change form just posted yesterday so folks need some time review the footnotes. Comments due by noon Friday 2/9 due to printing deadline.

2/8/18 Erick VanDyke via email: “The operating limit content seems useful. Would like to see the flow values remain in cfs not kcfs, as has been the measure used in the past.”

Record of Final Action: APPROVED as revised to change kcfs to cfs 2/8/18

Table BON-14. Bonneville Dam Powerhouse One a

| Project | PH1 Units 1–10 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Best Operating Point (BOP) |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 35 | 18.9 | 7,203 | 23.6 | 9,019 | 27.3 | 10,527 | 31.8 | 12,960 |
| 36 | 19.5 | 7,205 | 24.3 | 8,985 | 28.3 | 10,564 | 33.0 | 12,997 |
| 37 | 20.1 | 7,205 | 25.0 | 8,951 | 29.2 | 10,598 | 34.1 | 13,028 |
| 38 | 20.7 | 7,204 | 25.6 | 8,918 | 30.2 | 10,627 | 35.3 | 13,054 |
| 39 | 21.3 | 7,202 | 26.3 | 8,886 | 31.2 | 10,654 | 36.4 | 13,076 |
| 40 | 21.9 | 7,199 | 26.9 | 8,854 | 32.1 | 10,677 | 37.6 | 13,093 |
| 41 | 22.5 | 7,201 | 28.0 | 8,969 | 33.2 | 10,759 | 38.8 | 13,147 |
| 42 | 23.1 | 7,202 | 29.1 | 9,077 | 34.3 | 10,837 | 40.0 | 13,197 |
| 43 | 23.6 | 7,203 | 30.1 | 9,180 | 35.4 | 10,910 | 41.1 | 13,242 |
| 44 | 24.2 | 7,203 | 31.2 | 9,278 | 36.5 | 10,979 | 42.3 | 13,284 |
| 45 | 24.8 | 7,203 | 32.3 | 9,370 | 37.6 | 11,045 | 43.5 | 13,322 |
| 46 | 25.4 | 7,210 | 33.2 | 9,416 | 38.8 | 11,109 | 44.6 | 13,303 |
| 47 | 26.0 | 7,217 | 34.1 | 9,459 | 39.9 | 11,170 | 45.7 | 13,280 |
| 48 | 26.6 | 7,223 | 35.0 | 9,500 | 41.0 | 11,227 | 46.7 | 13,253 |
| 49 | 27.3 | 7,229 | 36.0 | 9,539 | 42.1 | 11,282 | 47.8 | 13,222 |
| 50 | 27.9 | 7,234 | 36.9 | 9,575 | 43.2 | 11,333 | 48.8 | 13,188 |
| 51 | 28.5 | 7,241 | 37.8 | 9,618 | 44.2 | 11,356 | 49.9 | 13,207 |
| 52 | 29.1 | 7,248 | 38.4 | 9,577 | 45.2 | 11,378 | 51.0 | 13,222 |
| 53 | 29.7 | 7,254 | 39.0 | 9,537 | 46.2 | 11,398 | 52.1 | 13,234 |
| 54 | 30.3 | 7,260 | 39.7 | 9,499 | 47.2 | 11,418 | 53.1 | 13,242 |
| 55 | 30.9 | 7,266 | 41.6 | 9,768 | 48.2 | 11,465 | 54.2 | 13,248 |
| 56 | 31.5 | 7,269 | 42.5 | 9,808 | 49.2 | 11,478 | 54.6 | 13,046 |
| 57 | 32.1 | 7,272 | 43.4 | 9,846 | 50.3 | 11,518 | 54.9 | 12,841 |
| 58 | 32.7 | 7,274 | 44.4 | 9,883 | 51.4 | 11,557 | 55.3 | 12,633 |
| 59 | 33.3 | 7,277 | 45.3 | 9,918 | 52.4 | 11,594 | 55.5 | 12,421 |
| 60 | 33.8 | 7,279 | 46.3 | 9,952 | 53.5 | 11,630 | 55.8 | 12,206 |
| 61 | 34.5 | 7,296 | 46.9 | 9,930 | 54.3 | 11,610 | 56.1 | 12,048 |
| 62 | 35.1 | 7,311 | 47.6 | 9,909 | 55.1 | 11,591 | 56.3 | 11,887 |
| 63 | 35.8 | 7,326 | 48.3 | 9,889 | 56.0 | 11,572 | 56.5 | 11,721 |
| 64 | 36.5 | 7,340 | 49.0 | 9,868 | 56.6 | 11,519 | 56.7 | 11,552 |
| 65 | 37.1 | 7,354 | 49.7 | 9,849 | 56.8 | 11,388 | 56.8 | 11,379 |
| 66 | 37.6 | 7,341 | 50.6 | 9,876 | 57.1 | 11,265 | 57.4 | 11,328 |
| 67 | 38.1 | 7,329 | 51.4 | 9,902 | 57.3 | 11,124 | 58.1 | 11,275 |
| 68 | 38.6 | 7,317 | 52.3 | 9,928 | 57.6 | 11,021 | 58.6 | 11,220 |
| 69 | 39.0 | 7,305 | 53.2 | 9,954 | 57.8 | 10,896 | 59.2 | 11,161 |
| 70 | 39.5 | 7,294 | 54.1 | 9,979 | 58.0 | 10,736 | 59.8 | 11,100 |

- Table values derived from HDC report (June 2000), except "Best Operating Point" derived from Turbine Survival Program (TSP) modeling and analysis (Jan 2013). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on the cavitation or generator limit (added Feb 2018).

Table BON-15. Bonneville Dam Powerhouse Two a

| Project | PH2 Units 11-18 - With STS |  |  |  |  |  | PH2 Units 11-18 - No STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (ft) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 35 | 27.6 | 11,259 | 44.3 | 18,068 | 46.7 | 19,283 | 28.2 | 11,444 | 45.1 | 18,277 | 46.7 | 19,168 |
| 36 | 28.5 | 11,271 | 45.8 | 18,097 | 49.0 | 19,714 | 29.2 | 11,455 | 46.6 | 18,306 | 49.0 | 19,597 |
| 37 | 29.4 | 11,279 | 47.3 | 18,121 | 51.4 | 20,146 | 30.1 | 11,464 | 48.1 | 18,331 | 51.4 | 20,026 |
| 38 | 30.3 | 11,284 | 48.8 | 18,139 | 53.9 | 20,580 | 31.0 | 11,470 | 49.7 | 18,350 | 53.9 | 20,457 |
| 39 | 31.3 | 11,287 | 50.3 | 18,153 | 56.4 | 21,014 | 32.0 | 11,473 | 51.2 | 18,364 | 56.4 | 20,889 |
| 40 | 32.2 | 11,288 | 51.8 | 18,162 | 59.0 | 21,450 | 32.9 | 11,474 | 52.7 | 18,374 | 59.0 | 21,321 |
| 41 | 33.0 | 11,259 | 53.3 | 18,197 | 61.2 | 21,654 | 33.7 | 11,445 | 54.3 | 18,409 | 61.2 | 21,535 |
| 42 | 33.8 | 11,230 | 54.9 | 18,228 | 63.4 | 21,854 | 34.6 | 11,415 | 55.8 | 18,441 | 63.4 | 21,744 |
| 43 | 34.6 | 11,201 | 56.4 | 18,255 | 65.6 | 22,049 | 35.4 | 11,386 | 57.4 | 18,468 | 65.6 | 21,949 |
| 44 | 35.4 | 11,172 | 57.9 | 18,278 | 67.8 | 22,240 | 36.2 | 11,357 | 58.9 | 18,493 | 67.8 | 22,150 |
| 45 | 36.2 | 11,144 | 59.4 | 18,299 | 70.1 | 22,427 | 37.0 | 11,328 | 60.5 | 18,514 | 70.1 | 22,347 |
| 46 | 37.0 | 11,139 | 61.0 | 18,366 | 72.1 | 22,441 | 37.9 | 11,324 | 62.1 | 18,581 | 72.1 | 22,390 |
| 47 | 37.8 | 11,135 | 61.9 | 18,200 | 74.2 | 22,450 | 38.7 | 11,319 | 63.0 | 18,415 | 74.2 | 22,429 |
| 48 | 38.7 | 11,129 | 62.7 | 18,040 | 76.3 | 22,455 | 39.6 | 11,314 | 63.8 | 18,255 | 76.3 | 22,463 |
| 49 | 39.5 | 11,124 | 63.5 | 17,887 | 76.5 | 21,994 | 40.4 | 11,308 | 64.7 | 18,101 | 76.5 | 22,040 |
| 50 | 40.3 | 11,118 | 67.5 | 18,598 | 76.5 | 21,497 | 41.3 | 11,303 | 68.7 | 18,817 | 76.5 | 21,527 |
| 51 | 41.3 | 11,154 | 69.8 | 18,850 | 76.5 | 20,999 | 42.2 | 11,339 | 71.1 | 19,072 | 76.5 | 21,015 |
| 52 | 42.3 | 11,187 | 72.1 | 19,091 | 76.5 | 20,502 | 43.2 | 11,373 | 73.4 | 19,316 | 76.5 | 20,502 |
| 53 | 43.2 | 11,219 | 74.5 | 19,323 | 76.5 | 20,005 | 44.2 | 11,405 | 75.8 | 19,551 | 76.5 | 19,989 |
| 54 | 44.2 | 11,249 | 76.5 b | 19,536 | 76.5 | 19,536 | 45.2 | 11,436 | 76.5 b | 19,431 | 76.5 | 19,431 |
| 55 | 45.2 | 11,278 | 76.5 b | 19,115 | 76.5 | 19,115 | 46.2 | 11,466 | 76.5 b | 18,975 | 76.5 | 18,975 |
| 56 | 46.4 | 11,343 | 76.5 b | 18,718 | 76.5 | 18,718 | 47.4 | 11,531 | 76.5 b | 18,581 | 76.5 | 18,581 |
| 57 | 47.6 | 11,404 | 76.5 b | 18,336 | 76.5 | 18,336 | 48.6 | 11,593 | 76.5 b | 18,202 | 76.5 | 18,202 |
| 58 | 48.8 | 11,461 | 76.5 b | 17,967 | 76.5 | 17,967 | 49.9 | 11,652 | 76.5 b | 17,836 | 76.5 | 17,836 |
| 59 | 50.0 | 11,515 | 76.5 b | 17,611 | 76.5 | 17,611 | 51.1 | 11,707 | 76.5 b | 17,483 | 76.5 | 17,483 |
| 60 | 51.2 | 11,567 | 76.5 b | 17,267 | 76.5 | 17,267 | 52.3 | 11,760 | 76.5 b | 17,142 | 76.5 | 17,142 |
| 61 | 51.8 | 11,532 | 76.5 b | 16,978 | 76.5 | 16,978 | 53.0 | 11,724 | 76.5 b | 16,857 | 76.5 | 16,857 |
| 62 | 52.5 | 11,498 | 76.5 b | 16,699 | 76.5 | 16,699 | 53.7 | 11,690 | 76.5 b | 16,582 | 76.5 | 16,582 |
| 63 | 53.1 | 11,466 | 76.5 b | 16,428 | 76.5 | 16,428 | 54.3 | 11,657 | 76.5 b | 16,315 | 76.5 | 16,315 |
| 64 | 53.7 | 11,434 | 76.5 b | 16,166 | 76.5 | 16,166 | 55.0 | 11,625 | 76.5 b | 16,056 | 76.5 | 16,056 |
| 65 | 54.4 | 11,405 | 76.5 b | 15,912 | 76.5 | 15,912 | 55.6 | 11,595 | 76.5 b | 15,806 | 76.5 | 15,806 |
| 66 | 55.4 | 11,448 | 76.5 b | 15,671 | 76.5 | 15,671 | 56.7 | 11,639 | 76.5 b | 15,570 | 76.5 | 15,570 |
| 67 | 56.5 | 11,490 | 76.5 b | 15,437 | 76.5 | 15,437 | 57.8 | 11,682 | 76.5 b | 15,341 | 76.5 | 15,341 |
| 68 | 57.5 | 11,532 | 76.5 b | 15,210 | 76.5 | 15,210 | 58.9 | 11,724 | 76.5 b | 15,119 | 76.5 | 15,119 |
| 69 | 58.6 | 11,571 | 76.5 b | 14,990 | 76.5 | 14,990 | 59.9 | 11,764 | 76.5 b | 14,903 | 76.5 | 14,903 |
| 70 | 59.6 | 11,610 | 76.5 b | 14,775 | 76.5 | 14,775 | 61.0 | 11,803 | 76.5 b | 14,693 | 76.5 | 14,693 |

- Table values derived from HDC report (Dec 2005). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on cavitation or generator limit (added Feb 2018).

- At project head ≥ 54 ft, BON PH2 units are restricted by the Operating Limit of 76.5 MW and cannot achieve the modeled upper limit of the 1% turbine efficiency range. Power (MW) and flow (cfs) values shown are at the Operating Limit, not the 1% upper limit.

Table TDA-6. The Dalles Dam a

| Project | TDA Units 1–14 |  |  |  |  |  | TDA Units 15–22 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 55 | 35.1 | 8,854 | 44.1 | 11,108 | 61.3 | 16,600 | 38.5 | 9,643 | 49.3 | 12,346 | 71.7 | 18,942 |
| 56 | 35.9 | 8,875 | 45.1 | 11,147 | 62.8 | 16,639 | 39.0 | 9,554 | 50.6 | 12,402 | 73.5 | 18,997 |
| 57 | 36.7 | 8,894 | 46.2 | 11,184 | 64.2 | 16,675 | 39.4 | 9,468 | 51.9 | 12,454 | 75.2 | 19,049 |
| 58 | 37.5 | 8,912 | 47.2 | 11,219 | 65.7 | 16,709 | 39.9 | 9,384 | 53.2 | 12,503 | 76.9 | 19,098 |
| 59 | 38.3 | 8,929 | 48.3 | 11,252 | 67.1 | 16,740 | 40.4 | 9,302 | 54.4 | 12,548 | 78.7 | 19,145 |
| 60 | 39.1 | 8,945 | 49.4 | 11,282 | 68.6 | 16,769 | 40.8 | 9,223 | 55.7 | 12,590 | 80.5 | 19,189 |
| 61 | 39.5 | 8,870 | 50.8 | 11,415 | 70.0 | 16,803 | 41.6 | 9,219 | 56.8 | 12,599 | 82.2 | 19,254 |
| 62 | 39.9 | 8,798 | 52.3 | 11,543 | 71.4 | 16,834 | 42.3 | 9,215 | 57.9 | 12,607 | 83.9 | 19,316 |
| 63 | 40.3 | 8,728 | 53.8 | 11,665 | 72.9 | 16,862 | 43.0 | 9,211 | 58.9 | 12,613 | 85.6 | 19,376 |
| 64 | 40.7 | 8,660 | 55.3 | 11,783 | 74.3 | 16,889 | 43.8 | 9,207 | 60.0 | 12,619 | 87.3 | 19,433 |
| 65 | 41.0 | 8,593 | 56.8 | 11,896 | 75.7 | 16,913 | 44.5 | 9,202 | 61.1 | 12,624 | 89.0 | 19,488 |
| 66 | 41.8 | 8,614 | 58.0 | 11,939 | 77.2 | 16,953 | 45.1 | 9,164 | 62.5 | 12,719 | 90.8 | 19,528 |
| 67 | 42.6 | 8,633 | 59.2 | 11,980 | 78.7 | 16,992 | 45.6 | 9,127 | 64.0 | 12,810 | 92.5 | 19,566 |
| 68 | 43.4 | 8,652 | 60.3 | 12,019 | 80.2 | 17,029 | 46.1 | 9,091 | 65.5 | 12,899 | 94.2 | 19,602 |
| 69 | 44.2 | 8,670 | 61.5 | 12,056 | 81.7 | 17,063 | 46.7 | 9,056 | 66.9 | 12,984 | 95.9 | 19,636 |
| 70 | 45.0 | 8,686 | 62.7 | 12,092 | 83.2 | 17,096 | 47.2 | 9,021 | 68.4 | 13,066 | 97.6 | 19,667 |
| 71 | 45.8 | 8,693 | 63.7 | 12,111 | 84.2 | 17,009 | 47.9 | 9,019 | 70.0 | 13,168 | 98.7 | 19,501 |
| 72 | 46.5 | 8,700 | 64.5 | 12,067 | 85.1 | 16,920 | 48.6 | 9,016 | 70.6 | 13,105 | 98.7 | 19,141 |
| 73 | 47.2 | 8,706 | 65.2 | 12,024 | 86.1 | 16,827 | 49.3 | 9,014 | 71.3 | 13,043 | 98.7 | 18,792 |
| 74 | 47.9 | 8,712 | 65.9 | 11,982 | 87.0 | 16,733 | 50.0 | 9,011 | 72.0 | 12,983 | 98.7 | 18,453 |
| 75 | 48.6 | 8,717 | 68.0 | 12,179 | 87.9 | 16,635 | 50.7 | 9,008 | 76.2 | 13,542 | 98.7 | 18,123 |
| 76 | 49.1 | 8,673 | 69.2 | 12,226 | 88.9 | 16,526 | 51.3 | 8,984 | 77.8 | 13,638 | 98.7 | 17,824 |
| 77 | 49.5 | 8,629 | 70.4 | 12,270 | 89.7 | 16,379 | 51.8 | 8,960 | 79.4 | 13,731 | 98.7 | 17,533 |
| 78 | 49.9 | 8,587 | 71.6 | 12,314 | 89.7 | 16,091 | 52.4 | 8,936 | 81.0 | 13,821 | 98.7 | 17,249 |
| 79 | 50.4 | 8,545 | 72.8 | 12,356 | 89.7 | 15,810 | 53.0 | 8,913 | 82.6 | 13,908 | 98.7 | 16,973 |
| 80 | 50.8 | 8,505 | 74.0 | 12,396 | 89.7 | 15,537 | 53.5 | 8,891 | 84.3 | 13,993 | 98.7 | 16,704 |
| 81 | 51.4 | 8,493 | 75.4 | 12,471 | 89.7 | 15,285 | 54.2 | 8,896 | 85.9 | 14,092 | 98.7 | 16,465 |
| 82 | 52.0 | 8,482 | 76.8 | 12,543 | 89.7 | 15,040 | 54.9 | 8,902 | 87.5 | 14,188 | 98.7 | 16,231 |
| 83 | 52.5 | 8,471 | 78.2 | 12,613 | 89.7 | 14,802 | 55.6 | 8,908 | 89.2 | 14,283 | 98.7 | 16,004 |
| 84 | 53.1 | 8,460 | 79.6 | 12,681 | 89.7 | 14,569 | 56.3 | 8,914 | 90.8 | 14,375 | 98.7 | 15,781 |
| 85 | 53.7 | 8,449 | 81.0 | 12,748 | 89.7 | 14,343 | 57.0 | 8,919 | 92.4 | 14,465 | 98.7 | 15,564 |
| 86 | 54.3 | 8,441 | 82.5 | 12,833 | 89.7 | 14,134 | 57.5 | 8,898 | 94.1 | 14,564 | 98.7 | 15,363 |
| 87 | 54.9 | 8,433 | 84.0 | 12,916 | 89.7 | 13,931 | 58.0 | 8,877 | 95.8 | 14,660 | 98.7 | 15,166 |
| 88 | 55.5 | 8,425 | 85.6 | 12,997 | 89.7 | 13,733 | 58.5 | 8,856 | 97.4 | 14,755 | 98.7 | 14,974 |
| 89 | 56.0 | 8,417 | 87.1 | 13,076 | 89.7 | 13,539 | 59.0 | 8,836 | 98.7 b | 14,786 | 98.7 | 14,786 |
| 90 | 56.6 | 8,409 | 88.6 | 13,154 | 89.7 | 13,350 | 59.5 | 8,817 | 98.7 b | 14,602 | 98.7 | 14,602 |
| 91 | 57.3 | 8,411 | 89.7 b | 13,236 | 89.7 | 13,192 | 60.1 | 8,815 | 98.7 b | 14,429 | 98.7 | 14,429 |
| 92 | 57.9 | 8,414 | 89.7 b | 13,080 | 89.7 | 13,037 | 60.8 | 8,813 | 98.7 b | 14,260 | 98.7 | 14,260 |
| 93 | 58.6 | 8,416 | 89.7 b | 12,928 | 89.7 | 12,885 | 61.4 | 8,811 | 98.7 b | 14,094 | 98.7 | 14,094 |
| 94 | 59.2 | 8,418 | 89.7 b | 12,779 | 89.7 | 12,737 | 62.1 | 8,809 | 98.7 b | 13,932 | 98.7 | 13,932 |
| 95 | 59.8 | 8,420 | 89.7 b | 12,634 | 89.7 | 12,592 | 62.7 | 8,808 | 98.7 b | 13,773 | 98.7 | 13,773 |

- Table values derived from HDC reports for Units 1-14 (Jan 2001) and Units 15-22 (Oct 2002). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on cavitation or generator limit (added Feb 2018).

- At project head ≥ 91 ft (TDA Units 1-14) and ≥ 89 ft (TDA Units 15-22), units are restricted by the Operating Limit and cannot achieve the modeled upper limit of the 1% turbine efficiency range. Power (MW) and flow (cfs) values shown are at the Operating Limit, not the 1% upper limit.

Table JDA-7. John Day Dam a

| Project | JDA Units 1-16 b - With STS |  |  |  |  |  | JDA Units 1-16 b - No STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 80 | 65.4 | 11,338 | 118.0 | 20,472 | 129.9 | 23,194 | 71.7 | 12,305 | 122.8 | 21,074 | 129.9 | 22,684 |
| 81 | 66.7 | 11,416 | 120.8 | 20,671 | 132.1 | 23,228 | 73.2 | 12,391 | 125.7 | 21,290 | 132.1 | 22,697 |
| 82 | 68.1 | 11,492 | 123.6 | 20,864 | 134.3 | 23,261 | 74.7 | 12,473 | 128.7 | 21,500 | 134.3 | 22,710 |
| 83 | 69.4 | 11,566 | 126.4 | 21,052 | 136.5 | 23,292 | 76.1 | 12,554 | 131.6 | 21,703 | 136.5 | 22,720 |
| 84 | 70.8 | 11,638 | 129.1 | 21,234 | 138.7 | 23,321 | 77.6 | 12,631 | 134.6 | 21,901 | 138.7 | 22,730 |
| 85 | 72.1 | 11,707 | 131.9 | 21,411 | 140.9 | 23,349 | 79.1 | 12,707 | 137.5 | 22,093 | 140.9 | 22,738 |
| 86 | 72.9 | 11,692 | 134.7 | 21,593 | 142.7 | 23,282 | 80.0 | 12,690 | 140.1 | 22,223 | 142.7 | 22,722 |
| 87 | 73.7 | 11,676 | 137.5 | 21,770 | 144.5 | 23,214 | 80.9 | 12,674 | 142.6 | 22,349 | 144.5 | 22,704 |
| 88 | 74.5 | 11,661 | 140.2 | 21,942 | 146.2 | 23,145 | 81.7 | 12,657 | 145.1 | 22,471 | 146.2 | 22,684 |
| 89 | 75.3 | 11,646 | 143.0 | 22,110 | 148.0 | 23,074 | 82.6 | 12,641 | 147.6 | 22,591 | 148.0 | 22,662 |
| 90 | 76.1 | 11,632 | 145.8 | 22,274 | 149.7 | 23,001 | 83.5 | 12,625 | 150.2 | 22,707 | 149.7 | 22,638 |
| 91 | 77.0 | 11,622 | 146.9 | 22,164 | 151.1 | 22,917 | 84.5 | 12,616 | 151.7 | 22,656 | 151.1 | 22,562 |
| 92 | 77.9 | 11,613 | 148.0 | 22,057 | 152.5 | 22,831 | 85.5 | 12,606 | 153.2 | 22,606 | 152.5 | 22,484 |
| 93 | 78.8 | 11,604 | 149.1 | 21,951 | 153.8 | 22,743 | 86.4 | 12,596 | 154.8 | 22,556 | 153.8 | 22,403 |
| 94 | 79.7 | 11,595 | 150.2 | 21,848 | 155.1 | 22,652 | 87.4 | 12,586 | 155.2 c | 22,321 | 155.1 | 22,321 |
| 95 | 80.6 | 11,585 | 151.3 | 21,746 | 155.2 | 22,383 | 88.4 | 12,576 | 155.2 c | 22,062 | 155.2 | 22,062 |
| 96 | 81.7 | 11,604 | 151.6 | 21,532 | 155.2 | 22,115 | 89.6 | 12,597 | 155.2 c | 21,797 | 155.2 | 21,797 |
| 97 | 82.8 | 11,623 | 151.8 | 21,323 | 155.2 | 21,852 | 90.8 | 12,617 | 155.2 c | 21,538 | 155.2 | 21,538 |
| 98 | 83.8 | 11,640 | 152.1 | 21,118 | 155.2 | 21,595 | 92.0 | 12,636 | 155.2 c | 21,284 | 155.2 | 21,284 |
| 99 | 84.9 | 11,657 | 152.4 | 20,917 | 155.2 | 21,343 | 93.1 | 12,655 | 155.2 c | 21,035 | 155.2 | 21,035 |
| 100 | 86.0 | 11,674 | 152.7 | 20,720 | 155.2 | 21,096 | 94.3 | 12,673 | 155.2 c | 20,792 | 155.2 | 20,792 |
| 101 | 86.9 | 11,675 | 154.9 | 20,800 | 155.2 | 20,852 | 95.3 | 12,675 | 155.2 c | 20,554 | 155.2 | 20,554 |
| 102 | 87.9 | 11,677 | 155.2 c | 20,613 | 155.2 | 20,613 | 96.4 | 12,676 | 155.2 c | 20,321 | 155.2 | 20,321 |
| 103 | 88.8 | 11,678 | 155.2 c | 20,378 | 155.2 | 20,378 | 97.4 | 12,678 | 155.2 c | 20,092 | 155.2 | 20,092 |
| 104 | 89.7 | 11,679 | 155.2 c | 20,149 | 155.2 | 20,149 | 98.4 | 12,679 | 155.2 c | 19,868 | 155.2 | 19,868 |
| 105 | 90.6 | 11,680 | 155.2 c | 19,923 | 155.2 | 19,923 | 99.4 | 12,680 | 155.2 c | 19,649 | 155.2 | 19,649 |
| 106 | 91.4 | 11,658 | 155.2 c | 19,711 | 155.2 | 19,711 | 100.2 | 12,656 | 155.2 c | 19,442 | 155.2 | 19,442 |
| 107 | 92.1 | 11,637 | 155.2 c | 19,503 | 155.2 | 19,503 | 101.0 | 12,633 | 155.2 c | 19,239 | 155.2 | 19,239 |
| 108 | 92.8 | 11,615 | 155.2 c | 19,299 | 155.2 | 19,299 | 101.8 | 12,610 | 155.2 c | 19,040 | 155.2 | 19,040 |
| 109 | 93.6 | 11,594 | 155.2 c | 19,098 | 155.2 | 19,098 | 102.6 | 12,587 | 155.2 c | 18,845 | 155.2 | 18,845 |
| 110 | 94.3 | 11,574 | 155.2 c | 18,901 | 155.2 | 18,901 | 103.5 | 12,565 | 155.2 c | 18,653 | 155.2 | 18,653 |

- Table values derived from HDC report (Nov 2002). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on cavitation or generator limit (added Feb 2018).

- As of February 2018, Units 4, 8, 9, 11, and 12 have fixed blades and a restricted operating range of approximately 17-19 kcfs.

- At project head ≥ 102 ft (with STS) and ≥ 94 ft (no STS), JDA units are restricted by the Operating Limit and cannot achieve the modeled upper limit of the 1% turbine efficiency range. Power (MW) and flow (cfs) values shown are at the Operating Limit, not the 1% upper limit.

Table MCN-6. McNary Dam a

| Project | With ESBS |  |  |  |  |  | No ESBS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 62 | 34.5 | 7,951 | 49.7 | 11,454 | 68.0 | 16,311 | 34.7 | 7754 | 50.8 | 11,346 | 68.0 | 15,710 |
| 63 | 35.2 | 7,963 | 51.0 | 11,552 | 69.6 | 16,399 | 35.4 | 7765 | 52.1 | 11,444 | 69.6 | 15,793 |
| 64 | 35.8 | 7,974 | 52.3 | 11,646 | 71.2 | 16,486 | 36.0 | 7776 | 53.5 | 11,537 | 71.2 | 15,875 |
| 65 | 36.5 | 7,984 | 53.7 | 11,736 | 72.8 | 16,571 | 36.7 | 7,786 | 54.8 | 11,627 | 72.8 | 15,955 |
| 66 | 37.0 | 7,959 | 55.2 | 11,869 | 74.1 | 16,574 | 37.2 | 7,762 | 56.3 | 11,759 | 74.1 | 15,945 |
| 67 | 37.5 | 7,934 | 56.7 | 11,997 | 75.3 | 16,574 | 37.7 | 7,739 | 57.9 | 11,887 | 75.3 | 15,933 |
| 68 | 38.0 | 7,911 | 58.2 | 12,121 | 76.6 | 16,572 | 38.2 | 7,716 | 59.4 | 12,009 | 76.6 | 15,919 |
| 69 | 38.5 | 7,887 | 59.7 | 12,240 | 77.8 | 16,567 | 38.7 | 7,694 | 60.9 | 12,128 | 77.8 | 15,903 |
| 70 | 39.0 | 7,864 | 61.2 | 12,355 | 79.0 | 16,560 | 39.2 | 7,671 | 62.5 | 12,243 | 79.0 | 15,884 |
| 71 | 39.6 | 7,874 | 62.1 | 12,355 | 79.7 | 16,433 | 39.8 | 7,681 | 63.4 | 12,243 | 79.7 | 15,782 |
| 72 | 40.2 | 7,883 | 63.1 | 12,354 | 80.4 | 16,303 | 40.4 | 7,691 | 64.4 | 12,242 | 80.4 | 15,676 |
| 73 | 40.9 | 7,892 | 64.0 | 12,353 | 81.0 | 16,169 | 41.1 | 7,699 | 65.3 | 12,241 | 81.0 | 15,567 |
| 74 | 41.5 | 7,901 | 64.9 | 12,351 | 81.6 | 16,033 | 41.7 | 7,708 | 66.3 | 12,240 | 81.3 | 15,455 |
| 75 | 42.2 | 7,909 | 65.8 | 12,350 | 82.2 | 15,893 | 42.4 | 7,716 | 67.2 | 12,239 | 81.3 | 15,340 |
| 76 | 42.8 | 7,907 | 66.4 | 12,282 | 82.5 | 15,705 | 43.0 | 7,714 | 67.9 | 12,172 | 81.3 | 15,161 |
| 77 | 43.4 | 7,905 | 67.1 | 12,216 | 82.8 | 15,513 | 43.6 | 7,713 | 68.5 | 12,107 | 81.3 | 14,979 |
| 78 | 44.0 | 7,903 | 67.7 | 12,151 | 83.1 | 15,319 | 44.2 | 7,711 | 69.1 | 12,044 | 81.3 | 14,795 |
| 79 | 44.6 | 7,900 | 68.3 | 12,088 | 83.3 | 15,122 | 44.8 | 7,709 | 69.7 | 11,981 | 81.3 | 14,608 |
| 80 | 45.2 | 7,897 | 68.9 | 12,026 | 83.4 | 14,922 | 45.5 | 7,706 | 70.3 | 11,920 | 81.3 | 14,418 |
| 81 | 45.9 | 7,911 | 70.0 | 12,067 | 83.7 | 14,747 | 46.1 | 7,720 | 71.5 | 11,961 | 81.3 | 14,256 |
| 82 | 46.5 | 7,925 | 71.1 | 12,106 | 83.8 | 14,569 | 46.8 | 7,734 | 72.6 | 12,000 | 81.3 | 14,091 |
| 83 | 47.2 | 7,939 | 72.2 | 12,145 | 84.0 | 14,389 | 47.4 | 7,747 | 73.7 | 12,038 | 81.3 | 13,924 |
| 84 | 47.9 | 7,952 | 73.3 | 12,182 | 84.1 | 14,206 | 48.1 | 7,759 | 74.9 | 12,076 | 81.3 | 13,754 |
| 85 | 48.5 | 7,964 | 74.4 | 12,219 | 84.2 | 14,020 | 48.8 | 7,772 | 76.0 | 12,112 | 81.3 | 13,582 |
| 86 | 49.2 | 7,987 | 75.1 | 12,179 | 84.0 | 13,806 | 49.5 | 7,794 | 76.7 | 12,073 | 81.3 | 13,373 |
| 87 | 50.0 | 8,008 | 75.7 | 12,140 | 83.8 | 13,588 | 50.2 | 7,815 | 77.3 | 12,034 | 81.3 | 13,161 |

- Table values derived from HDC report (Mar 1999; updated Jan 2005). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on cavitation or generator limit (added Feb 2018).

Table IHR-5. Ice Harbor Dam a

| Project | IHR Unit 1 - With STS |  |  |  |  |  | IHR Unit 1 - No STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 85 | 51.7 | 8,417 | 83.6 | 13,590 | 92.8 | 16,053 | 51.9 | 8,340 | 89.9 | 14,452 | 102.6 | 16,859 |
| 86 | 52.6 | 8,443 | 84.6 | 13,585 | 94.3 | 16,077 | 52.7 | 8,367 | 91.0 | 14,447 | 103.1 | 16,715 |
| 87 | 53.4 | 8,469 | 85.6 | 13,580 | 95.7 | 16,099 | 53.5 | 8,392 | 92.0 | 14,441 | 103.5 | 16,568 |
| 88 | 54.2 | 8,494 | 86.6 | 13,574 | 97.3 | 16,144 | 54.3 | 8,417 | 93.1 | 14,436 | 103.5 | 16,420 |
| 89 | 55.0 | 8,518 | 87.6 | 13,569 | 99.0 | 16,187 | 55.1 | 8,441 | 94.2 | 14,430 | 103.5 | 16,252 |
| 90 | 55.8 | 8,542 | 88.6 | 13,563 | 100.1 | 16,158 | 55.9 | 8,465 | 95.3 | 14,424 | 103.5 | 16,034 |
| 91 | 56.5 | 8,548 | 89.8 | 13,585 | 101.0 | 16,058 | 56.6 | 8,471 | 96.5 | 14,448 | 103.5 | 15,822 |
| 92 | 57.1 | 8,554 | 90.9 | 13,607 | 101.9 | 15,960 | 57.3 | 8,477 | 97.8 | 14,471 | 103.5 | 15,614 |
| 93 | 57.8 | 8,559 | 92.1 | 13,628 | 102.8 | 15,864 | 58.0 | 8,482 | 99.0 | 14,494 | 103.5 | 15,411 |
| 94 | 58.5 | 8,565 | 93.2 | 13,649 | 103.5 | 15,769 | 58.6 | 8,488 | 100.3 | 14,516 | 103.5 | 15,213 |
| 95 | 59.2 | 8,570 | 94.4 | 13,669 | 103.5 | 15,675 | 59.3 | 8,493 | 101.5 | 14,537 | 103.5 | 15,019 |
| 96 | 59.9 | 8,589 | 95.3 | 13,662 | 103.5 | 15,425 | 60.1 | 8,511 | 102.5 | 14,530 | 103.5 | 14,845 |
| 97 | 60.7 | 8,607 | 96.3 | 13,655 | 103.5 | 15,180 | 60.8 | 8,529 | 103.5 b | 14,676 | 103.5 | 14,676 |
| 98 | 61.5 | 8,624 | 97.3 | 13,648 | 103.5 | 14,941 | 61.6 | 8,546 | 103.5 b | 14,509 | 103.5 | 14,509 |
| 99 | 62.2 | 8,641 | 98.2 | 13,641 | 103.5 | 14,708 | 62.4 | 8,563 | 103.5 b | 14,347 | 103.5 | 14,347 |
| 100 | 63.0 | 8,658 | 99.2 | 13,634 | 103.5 | 14,481 | 63.1 | 8,580 | 103.5 b | 14,187 | 103.5 | 14,187 |
| 101 | 64.0 | 8,707 | 99.9 | 13,590 | 103.5 | 14,318 | 64.1 | 8,629 | 103.5 b | 14,037 | 103.5 | 14,037 |
| 102 | 65.0 | 8,756 | 100.6 | 13,547 | 103.5 | 14,158 | 65.2 | 8,677 | 103.5 b | 13,890 | 103.5 | 13,890 |
| 103 | 66.0 | 8,804 | 101.3 | 13,505 | 103.5 | 14,001 | 66.2 | 8,725 | 103.5 b | 13,746 | 103.5 | 13,746 |
| 104 | 67.0 | 8,850 | 102.0 | 13,463 | 103.5 | 13,847 | 67.2 | 8,771 | 103.5 b | 13,605 | 103.5 | 13,605 |
| 105 | 68.0 | 8,896 | 102.6 | 13,422 | 103.5 | 13,697 | 68.2 | 8,816 | 103.5 b | 13,466 | 103.5 | 13,466 |
|  | IHR Unit 2c - With STS |  |  |  |  |  | IHR Unit 2c - No STS |  |  |  |  |  |
| 85 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 86 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 87 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 88 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 89 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 90 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 91 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 92 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 93 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 94 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 95 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 96 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 97 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 98 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 99 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 100 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 101 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 102 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 103 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 104 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 105 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |

| Project | IHR Unit 3d - With STS |  |  |  |  |  | IHR Unit 3d - No STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 85 | 69.8 | 11,404 | 74.1 | 12,100 | n/a | n/a | 70.9 | 11,452 | 75.2 | 12,141 | n/a | n/a |
| 86 | 70.8 | 11,423 | 75.0 | 12,098 | n/a | n/a | 71.9 | 11,471 | 76.1 | 12,140 | n/a | n/a |
| 87 | 71.8 | 11,442 | 75.9 | 12,097 | n/a | n/a | 72.9 | 11,490 | 77.0 | 12,139 | n/a | n/a |
| 88 | 72.8 | 11,460 | 76.8 | 12,096 | n/a | n/a | 73.9 | 11,508 | 77.9 | 12,137 | n/a | n/a |
| 89 | 73.8 | 11,477 | 77.7 | 12,094 | n/a | n/a | 74.9 | 11,526 | 78.9 | 12,136 | n/a | n/a |
| 90 | 74.7 | 11,494 | 78.6 | 12,092 | n/a | n/a | 75.9 | 11,542 | 79.8 | 12,134 | n/a | n/a |
| 91 | 75.9 | 11,544 | 80.1 | 12,184 | n/a | n/a | 77.1 | 11,593 | 81.3 | 12,226 | n/a | n/a |
| 92 | 77.1 | 11,593 | 81.6 | 12,274 | n/a | n/a | 78.3 | 11,642 | 82.8 | 12,316 | n/a | n/a |
| 93 | 78.3 | 11,641 | 83.1 | 12,362 | n/a | n/a | 79.5 | 11,690 | 84.4 | 12,404 | n/a | n/a |
| 94 | 79.5 | 11,688 | 84.6 | 12,447 | n/a | n/a | 80.7 | 11,737 | 85.9 | 12,490 | n/a | n/a |
| 95 | 80.6 | 11,734 | 86.1 | 12,531 | n/a | n/a | 81.9 | 11,783 | 87.4 | 12,575 | n/a | n/a |
| 96 | 81.1 | 11,683 | 86.5 | 12,452 | n/a | n/a | 82.4 | 11,732 | 87.8 | 12,495 | n/a | n/a |
| 97 | 81.7 | 11,633 | 86.9 | 12,374 | n/a | n/a | 82.9 | 11,682 | 88.2 | 12,417 | n/a | n/a |
| 98 | 82.2 | 11,584 | 87.2 | 12,297 | n/a | n/a | 83.5 | 11,633 | 88.5 | 12,340 | n/a | n/a |
| 99 | 82.7 | 11,536 | 87.6 | 12,223 | n/a | n/a | 84.0 | 11,585 | 88.9 | 12,265 | n/a | n/a |
| 100 | 83.2 | 11,489 | 88.0 | 12,149 | n/a | n/a | 84.5 | 11,537 | 89.3 | 12,192 | n/a | n/a |
| 101 | 84.1 | 11,500 | 89.0 | 12,168 | n/a | n/a | 85.4 | 11,549 | 90.3 | 12,210 | n/a | n/a |
| 102 | 85.0 | 11,511 | 90.0 | 12,186 | n/a | n/a | 86.4 | 11,560 | 91.4 | 12,229 | n/a | n/a |
| 103 | 85.9 | 11,522 | 91.0 | 12,204 | n/a | n/a | 87.3 | 11,571 | 92.4 | 12,247 | n/a | n/a |
| 104 | 86.9 | 11,533 | 92.0 | 12,222 | n/a | n/a | 88.2 | 11,582 | 93.4 | 12,265 | n/a | n/a |
| 105 | 87.8 | 11,544 | 93.1 | 12,239 | n/a | n/a | 89.2 | 11,593 | 94.5 | 12,282 | n/a | n/a |
|  | IHR Units 4, 5e, 6 - With STS |  |  |  |  |  | IHR Units 4, 5e, 6 - No STS |  |  |  |  |  |
| 85 | 58.9 | 9,369 | 93.1 | 14,810 | 121.8 | 20,745 | 62.0 | 9,745 | 110.7 | 17,413 | 121.8 | 19,401 |
| 86 | 59.7 | 9,380 | 94.4 | 14,824 | 122.7 | 20,569 | 62.8 | 9,756 | 112.3 | 17,430 | 122.7 | 19,283 |
| 87 | 60.6 | 9,390 | 95.7 | 14,838 | 123.4 | 20,392 | 63.7 | 9,767 | 113.8 | 17,447 | 123.4 | 19,162 |
| 88 | 61.4 | 9,400 | 97.0 | 14,851 | 124.2 | 20,212 | 64.5 | 9,777 | 115.3 | 17,462 | 124.2 | 19,039 |
| 89 | 62.2 | 9,410 | 98.2 | 14,864 | 124.9 | 20,034 | 65.4 | 9,787 | 116.8 | 17,477 | 124.9 | 18,905 |
| 90 | 63.0 | 9,419 | 99.5 | 14,876 | 125.6 | 19,747 | 66.3 | 9,797 | 118.3 | 17,492 | 125.6 | 18,752 |
| 91 | 63.7 | 9,416 | 100.7 | 14,885 | 126.2 | 19,569 | 67.0 | 9,794 | 119.8 | 17,503 | 126.2 | 18,599 |
| 92 | 64.5 | 9,414 | 102.0 | 14,895 | 126.9 | 19,389 | 67.8 | 9,792 | 121.3 | 17,515 | 126.9 | 18,445 |
| 93 | 65.2 | 9,411 | 103.2 | 14,904 | 127.2 | 19,159 | 68.6 | 9,789 | 122.7 | 17,525 | 127.2 | 18,242 |
| 94 | 65.9 | 9,409 | 104.5 | 14,912 | 127.2 | 18,893 | 69.3 | 9,787 | 124.2 | 17,535 | 127.2 | 18,004 |
| 95 | 66.6 | 9,406 | 105.7 | 14,921 | 127.2 | 18,633 | 70.1 | 9,784 | 125.7 | 17,545 | 127.2 | 17,771 |
| 96 | 67.5 | 9,416 | 106.7 | 14,892 | 127.2 | 18,396 | 70.9 | 9,794 | 126.8 | 17,512 | 127.2 | 17,560 |
| 97 | 68.3 | 9,425 | 107.7 | 14,864 | 127.2 | 18,165 | 71.8 | 9,804 | 127.2 b | 17,353 | 127.2 | 17,353 |
| 98 | 69.1 | 9,434 | 108.6 | 14,836 | 127.2 | 17,938 | 72.7 | 9,813 | 127.2 b | 17,150 | 127.2 | 17,150 |
| 99 | 69.9 | 9,442 | 109.6 | 14,809 | 127.2 | 17,717 | 73.5 | 9,822 | 127.2 b | 16,952 | 127.2 | 16,952 |
| 100 | 70.7 | 9,451 | 110.6 | 14,782 | 127.2 | 17,499 | 74.4 | 9,831 | 127.2 b | 16,757 | 127.2 | 16,757 |
| 101 | 71.4 | 9,446 | 112.9 | 14,939 | 127.2 | 17,251 | 75.1 | 9,825 | 127.2 b | 16,573 | 127.2 | 16,573 |
| 102 | 72.0 | 9,441 | 115.1 | 15,093 | 127.2 | 17,009 | 75.7 | 9,820 | 127.2 b | 16,393 | 127.2 | 16,393 |
| 103 | 72.7 | 9,436 | 117.4 | 15,244 | 127.2 | 16,771 | 76.4 | 9,815 | 127.2 b | 16,216 | 127.2 | 16,216 |
| 104 | 73.3 | 9,431 | 119.7 | 15,392 | 127.2 | 16,539 | 77.1 | 9,810 | 127.2 b | 16,042 | 127.2 | 16,042 |
| 105 | 74.0 | 9,426 | 121.9 | 15,538 | 127.2 | 16,312 | 77.8 | 9,805 | 127.2 b | 15,872 | 127.2 | 15,872 |

- Table values derived from HDC report (March 2007). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on cavitation or generator limit (added Feb 2018).

- At project head ≥ 97 ft, Units 1, 4, 5, and 6 with No STS are restricted by the Operating Limit and cannot achieve the modeled upper limit of the 1% range. Power (MW) and flow (cfs) values shown are at Operating Limit, not the 1% upper limit.

- Unit 2 is out of service through approximately spring 2018 for turbine replacement. Table will be revised pending index tests.

- Unit 3 has fixed blades and a restricted operating range of approximately 11.4-12.5 kcfs (HDC report March 2015), but is scheduled to go out of service for turbine replacement starting in spring 2018 after Unit 2 returns to service. Table will be revised after completion of U3 turbine replacement and index testing.

- Unit 5 has fixed blades and a restricted operating range of approximately 13.1-14.1 kcfs (from 2017 U5 abbreviated index test).

Table LMN-6. Lower Monumental Dam a

| Project | LMN Units 1b, 2c, 3c - With STS |  |  |  |  |  |  | LMN Units 1b, 2c, 3c - No STS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs |  | MW | cfs | MW | cfs | MW | cfs |  | MW | cfs | MW | cfs |
| 85 | 68.6 | 11,169 |  | 128.5 | 20,905 | 140.9 | 24,344 | 69.2 | 11,123 |  | 125.8 | 20,216 | 140.9 | 23,569 |
| 86 | 69.4 | 11,154 |  | 131.0 | 21,056 | 142.8 | 24,273 | 70.0 | 11,109 |  | 128.3 | 20,363 | 142.8 | 23,542 |
| 87 | 70.2 | 11,140 |  | 133.5 | 21,204 | 144.6 | 24,200 | 70.8 | 11,094 |  | 130.8 | 20,506 | 144.6 | 23,513 |
| 88 | 70.9 | 11,125 |  | 136.1 | 21,348 | 146.5 | 24,126 | 71.6 | 11,080 |  | 133.3 | 20,645 | 146.5 | 23,482 |
| 89 | 71.7 | 11,111 |  | 138.6 | 21,488 | 148.3 | 24,050 | 72.3 | 11,066 |  | 135.8 | 20,781 | 148.3 | 23,450 |
| 90 | 72.4 | 11,097 |  | 141.2 | 21,625 | 150.2 | 23,974 | 73.1 | 11,052 |  | 138.3 | 20,913 | 150.2 | 23,415 |
| 91 | 73.3 | 11,088 |  | 141.6 | 21,418 | 151.5 | 23,815 | 74.0 | 11,043 |  | 138.7 | 20,714 | 151.5 | 23,268 |
| 92 | 74.1 | 11,079 |  | 142.0 | 21,216 | 152.8 | 23,654 | 74.8 | 11,035 |  | 139.1 | 20,518 | 152.8 | 23,119 |
| 93 | 75.0 | 11,071 |  | 142.4 | 21,018 | 154.0 | 23,492 | 75.7 | 11,026 |  | 139.5 | 20,327 | 154.0 | 22,968 |
| 94 | 75.8 | 11,061 |  | 142.8 | 20,824 | 155.2 | 23,420 | 76.5 | 11,017 |  | 139.9 | 20,140 | 155.2 | 22,850 |
| 95 | 76.7 | 11,052 |  | 143.2 | 20,634 | 155.2 | 22,904 | 77.4 | 11,009 |  | 140.3 | 19,956 | 155.2 | 22,409 |
| 96 | 77.7 | 11,071 |  | 143.3 | 20,416 | 155.2 | 22,592 | 78.4 | 11,027 |  | 140.4 | 19,746 | 155.2 | 22,125 |
| 97 | 78.8 | 11,088 |  | 143.5 | 20,203 | 155.2 | 22,286 | 79.5 | 11,044 |  | 140.6 | 19,540 | 155.2 | 21,847 |
| 98 | 79.8 | 11,105 |  | 143.6 | 19,994 | 155.2 | 21,988 | 80.5 | 11,061 |  | 140.7 | 19,338 | 155.2 | 21,576 |
| 99 | 80.8 | 11,121 |  | 143.8 | 19,789 | 155.2 | 21,696 | 81.5 | 11,078 |  | 140.9 | 19,141 | 155.2 | 21,309 |
| 100 | 81.8 | 11,137 |  | 144.0 | 19,589 | 155.2 | 21,410 | 82.6 | 11,093 |  | 141.0 | 18,947 | 155.2 | 21,049 |
| 101 | 82.7 | 11,138 |  | 145.9 | 19,641 | 155.2 | 21,130 | 83.5 | 11,095 |  | 142.9 | 18,998 | 155.2 | 20,798 |
| 102 | 83.6 | 11,140 |  | 147.8 | 19,692 | 155.2 | 20,857 | 84.3 | 11,096 |  | 144.8 | 19,047 | 155.2 | 20,553 |
| 103 | 84.5 | 11,141 |  | 149.7 | 19,741 | 155.2 | 20,589 | 85.2 | 11,098 |  | 146.7 | 19,095 | 155.2 | 20,312 |
| 104 | 85.4 | 11,142 |  | 151.6 | 19,789 | 155.2 | 20,326 | 86.1 | 11,099 |  | 148.5 | 19,142 | 155.2 | 20,077 |
| 105 | 86.2 | 11,143 |  | 153.5 | 19,837 | 155.2 | 20,069 | 87.0 | 11,100 |  | 150.4 | 19,188 | 155.2 | 19,846 |
|  | LMN Units 4d, 5, 6 - With STS |  |  |  |  |  |  | LMN Units 4d, 5, 6 - No STS |  |  |  |  |  |  |
| 85 | 89.8 |  | 14,150 | 123.8 | 19,493 | 141.3 | 25,052 | 89.5 |  | 13,962 | 122.5 | 19,102 | 141.3 | 24,441 |
| 86 | 91.0 |  | 14,160 | 125.5 | 19,519 | 143.3 | 24,978 | 90.7 |  | 13,971 | 124.2 | 19,128 | 143.3 | 24,414 |
| 87 | 92.2 |  | 14,169 | 127.2 | 19,545 | 145.4 | 24,904 | 91.9 |  | 13,981 | 125.9 | 19,153 | 145.4 | 24,385 |
| 88 | 93.4 |  | 14,178 | 128.9 | 19,569 | 147.4 | 24,829 | 93.1 |  | 13,990 | 127.6 | 19,177 | 147.4 | 24,356 |
| 89 | 94.6 |  | 14,187 | 130.6 | 19,593 | 149.4 | 24,753 | 94.2 |  | 13,998 | 129.3 | 19,201 | 149.4 | 24,324 |
| 90 | 95.7 |  | 14,195 | 132.3 | 19,616 | 151.4 | 24,676 | 95.4 |  | 14,006 | 131.0 | 19,224 | 151.4 | 24,291 |
| 91 | 96.9 |  | 14,196 | 133.9 | 19,613 | 153.5 | 24,623 | 96.5 |  | 14,007 | 132.5 | 19,221 | 153.5 | 24,230 |
| 92 | 98.0 |  | 14,197 | 135.4 | 19,610 | 155.2 | 24,553 | 97.7 |  | 14,008 | 134.0 | 19,218 | 155.2 | 24,168 |
| 93 | 99.2 |  | 14,197 | 136.9 | 19,607 | 155.2 | 23,936 | 98.8 |  | 14,009 | 135.5 | 19,215 | 155.2 | 23,577 |
| 94 | 100.3 |  | 14,198 | 138.5 | 19,603 | 155.2 | 23,343 | 99.9 |  | 14,010 | 137.1 | 19,211 | 155.2 | 23,008 |
| 95 | 101.4 |  | 14,198 | 140.0 | 19,600 | 155.2 | 22,771 | 101.1 |  | 14,010 | 138.6 | 19,208 | 155.2 | 22,460 |
| 96 | 102.3 |  | 14,170 | 140.5 | 19,456 | 155.2 | 22,389 | 102.0 |  | 13,982 | 139.1 | 19,067 | 155.2 | 21,828 |
| 97 | 103.2 |  | 14,142 | 141.0 | 19,315 | 155.2 | 22,017 | 102.9 |  | 13,954 | 139.6 | 18,929 | 155.2 | 21,478 |
| 98 | 104.1 |  | 14,114 | 141.5 | 19,177 | 155.2 | 21,654 | 103.8 |  | 13,928 | 140.1 | 18,794 | 155.2 | 21,136 |
| 99 | 105.1 |  | 14,087 | 142.0 | 19,042 | 155.2 | 21,300 | 104.7 |  | 13,901 | 140.5 | 18,662 | 155.2 | 20,803 |
| 100 | 106.0 |  | 14,061 | 142.5 | 18,909 | 155.2 | 20,955 | 105.6 |  | 13,875 | 141.0 | 18,532 | 155.2 | 20,723 |
| 101 | 107.3 |  | 14,091 | 143.9 | 18,909 | 155.2 | 20,701 | 106.9 |  | 13,904 | 142.5 | 18,532 | 155.2 | 20,477 |
| 102 | 108.5 |  | 14,120 | 145.4 | 18,909 | 155.2 | 20,452 | 108.2 |  | 13,933 | 143.9 | 18,532 | 155.2 | 20,236 |
| 103 | 109.8 |  | 14,149 | 146.8 | 18,909 | 155.2 | 20,208 | 109.4 |  | 13,962 | 145.3 | 18,532 | 155.2 | 19,999 |
| 104 | 111.1 |  | 14,177 | 148.2 | 18,909 | 155.2 | 19,970 | 110.7 |  | 13,989 | 146.7 | 18,532 | 155.2 | 19,768 |
| 105 | 112.4 |  | 14,204 | 149.6 | 18,909 | 155.2 | 19,736 | 112.0 |  | 14,017 | 148.1 | 18,532 | 155.2 | 19,541 |

- Table values derived from HDC report (July 2003). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on cavitation or generator limit (added Feb 2018).

- Unit 1 was previously fixed-blade and is being restored to adjustable-blade with full 1% range (est. return to service spring 2018).

- Units 2 and 3 runner blades were hydraulically locked in September 2017 due to failed blade seals. Unit 2 is restricted to the lower 1% range (~11-13 kcfs) and Unit 3 is restricted to the upper 1% range (~18-20 kcfs) until the blade seals are replaced.

- Unit 4 runner blades were hydraulically locked in December 2017 due to failed blade seals and is restricted to the upper 1% range (~17-19 kcfs) until the blade seals are replaced (currently scheduled in FY2018).

Table LGS-6. Little Goose Dam a

| Project | LGS Units 1, 2, 3 - With ESBS |  |  |  |  |  |  | LGS Units 1, 2, 3 - No ESBS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs |  | MW | cfs | MW | cfs | MW | cfs |  | MW | cfs | MW | cfs |
| 85 | 69.6 | 11,396 |  | 111.5 | 18,269 | 140.9 | 24,614 | 70.5 | 11,320 |  | 124.5 | 20,006 | 140.9 | 23,431 |
| 86 | 70.3 | 11,381 |  | 113.7 | 18,402 | 142.9 | 24,614 | 71.3 | 11,305 |  | 127.0 | 20,152 | 142.9 | 23,442 |
| 87 | 71.1 | 11,366 |  | 115.9 | 18,531 | 144.8 | 24,613 | 72.0 | 11,290 |  | 129.5 | 20,293 | 144.8 | 23,451 |
| 88 | 71.9 | 11,351 |  | 118.1 | 18,657 | 146.7 | 24,610 | 72.8 | 11,276 |  | 131.9 | 20,431 | 146.7 | 23,458 |
| 89 | 72.6 | 11,336 |  | 120.3 | 18,779 | 148.7 | 24,605 | 73.6 | 11,262 |  | 134.4 | 20,566 | 148.7 | 23,464 |
| 90 | 73.4 | 11,322 |  | 122.5 | 18,898 | 150.6 | 24,598 | 74.4 | 11,247 |  | 136.9 | 20,696 | 150.6 | 23,467 |
| 91 | 74.3 | 11,313 |  | 122.9 | 18,717 | 151.8 | 24,460 | 75.3 | 11,239 |  | 137.3 | 20,499 | 151.8 | 23,327 |
| 92 | 75.1 | 11,304 |  | 123.2 | 18,540 | 153.0 | 24,319 | 76.1 | 11,230 |  | 137.7 | 20,306 | 153.0 | 23,185 |
| 93 | 76.0 | 11,295 |  | 123.6 | 18,367 | 154.1 | 24,176 | 77.0 | 11,221 |  | 138.0 | 20,116 | 154.1 | 23,041 |
| 94 | 76.9 | 11,285 |  | 123.9 | 18,197 | 155.2 | 23,961 | 77.9 | 11,212 |  | 138.4 | 19,931 | 155.2 | 22,934 |
| 95 | 77.7 | 11,276 |  | 124.3 | 18,031 | 155.2 | 23,547 | 78.7 | 11,203 |  | 138.8 | 19,750 | 155.2 | 22,563 |
| 96 | 78.8 | 11,294 |  | 124.4 | 17,841 | 155.2 | 23,210 | 79.8 | 11,222 |  | 139.0 | 19,541 | 155.2 | 22,267 |
| 97 | 79.8 | 11,312 |  | 124.6 | 17,654 | 155.2 | 22,881 | 80.9 | 11,240 |  | 139.1 | 19,338 | 155.2 | 21,977 |
| 98 | 80.9 | 11,329 |  | 124.7 | 17,472 | 155.2 | 22,559 | 81.9 | 11,257 |  | 139.3 | 19,138 | 155.2 | 21,693 |
| 99 | 81.9 | 11,346 |  | 124.8 | 17,293 | 155.2 | 22,245 | 83.0 | 11,274 |  | 139.4 | 18,942 | 155.2 | 21,416 |
| 100 | 82.9 | 11,361 |  | 125.0 | 17,117 | 155.2 | 21,937 | 84.0 | 11,290 |  | 139.6 | 18,751 | 155.2 | 21,144 |
| 101 | 83.8 | 11,363 |  | 126.6 | 17,163 | 155.2 | 21,634 | 84.9 | 11,291 |  | 141.4 | 18,801 | 155.2 | 20,883 |
| 102 | 84.7 | 11,364 |  | 128.3 | 17,207 | 155.2 | 21,337 | 85.8 | 11,293 |  | 143.3 | 18,850 | 155.2 | 20,627 |
| 103 | 85.6 | 11,365 |  | 129.9 | 17,250 | 155.2 | 21,047 | 86.7 | 11,294 |  | 145.1 | 18,897 | 155.2 | 20,376 |
| 104 | 86.5 | 11,367 |  | 131.6 | 17,293 | 155.2 | 20,762 | 87.6 | 11,295 |  | 147.0 | 18,944 | 155.2 | 20,131 |
| 105 | 87.4 | 11,367 |  | 133.2 | 17,334 | 155.2 | 20,484 | 88.5 | 11,296 |  | 148.8 | 18,989 | 155.2 | 19,890 |
|  | LGS Units 4, 5, 6 - With ESBS |  |  |  |  |  |  | LGS Units 4, 5, 6 - No ESBS |  |  |  |  |  |  |
| 85 | 87.1 |  | 13,880 | 119.6 | 19,076 | 141.3 | 24,621 | 86.4 |  | 13,479 | 122.2 | 19,052 | 141.3 | 24,411 |
| 86 | 88.2 |  | 13,890 | 121.3 | 19,102 | 143.3 | 24,702 | 87.6 |  | 13,488 | 123.9 | 19,078 | 143.3 | 24,527 |
| 87 | 89.3 |  | 13,899 | 122.9 | 19,127 | 145.4 | 24,781 | 88.7 |  | 13,497 | 125.6 | 19,104 | 145.4 | 24,642 |
| 88 | 90.5 |  | 13,908 | 124.6 | 19,151 | 147.4 | 24,859 | 89.8 |  | 13,506 | 127.2 | 19,128 | 147.4 | 24,756 |
| 89 | 91.6 |  | 13,916 | 126.3 | 19,174 | 149.4 | 24,936 | 91.0 |  | 13,514 | 128.9 | 19,151 | 149.4 | 24,868 |
| 90 | 92.8 |  | 13,924 | 127.9 | 19,196 | 151.4 | 25,010 | 92.1 |  | 13,522 | 130.6 | 19,174 | 151.4 | 24,979 |
| 91 | 93.9 |  | 13,925 | 129.4 | 19,193 | 153.5 | 24,931 | 93.2 |  | 13,523 | 132.1 | 19,171 | 153.5 | 24,840 |
| 92 | 95.0 |  | 13,925 | 130.9 | 19,190 | 155.2 | 24,786 | 94.3 |  | 13,524 | 133.7 | 19,168 | 155.2 | 24,636 |
| 93 | 96.1 |  | 13,926 | 132.4 | 19,186 | 155.2 | 24,377 | 95.4 |  | 13,524 | 135.2 | 19,165 | 155.2 | 24,172 |
| 94 | 97.2 |  | 13,926 | 133.9 | 19,183 | 155.2 | 23,904 | 96.5 |  | 13,525 | 136.7 | 19,162 | 155.2 | 23,631 |
| 95 | 98.3 |  | 13,926 | 135.3 | 19,179 | 155.2 | 23,421 | 97.6 |  | 13,525 | 138.2 | 19,158 | 155.2 | 22,957 |
| 96 | 99.2 |  | 13,898 | 135.8 | 19,038 | 155.2 | 23,046 | 98.4 |  | 13,498 | 138.7 | 19,018 | 155.2 | 21,828 |
| 97 | 100.0 |  | 13,871 | 136.3 | 18,900 | 155.2 | 22,679 | 99.3 |  | 13,472 | 139.2 | 18,880 | 155.2 | 21,378 |
| 98 | 100.9 |  | 13,844 | 136.8 | 18,765 | 155.2 | 22,322 | 100.2 |  | 13,446 | 139.7 | 18,745 | 155.2 | 20,941 |
| 99 | 101.8 |  | 13,818 | 137.3 | 18,633 | 155.2 | 21,973 | 101.1 |  | 13,420 | 140.2 | 18,613 | 155.2 | 20,518 |
| 100 | 102.7 |  | 13,791 | 137.8 | 18,503 | 155.2 | 21,633 | 101.9 |  | 13,395 | 140.7 | 18,484 | 155.2 | 20,677 |
| 101 | 103.9 |  | 13,821 | 139.1 | 18,503 | 155.2 | 21,335 | 103.2 |  | 13,423 | 142.1 | 18,484 | 155.2 | 20,436 |
| 102 | 105.2 |  | 13,849 | 140.5 | 18,503 | 155.2 | 21,043 | 104.4 |  | 13,451 | 143.5 | 18,484 | 155.2 | 20,200 |
| 103 | 106.4 |  | 13,878 | 141.9 | 18,503 | 155.2 | 20,758 | 105.7 |  | 13,478 | 144.9 | 18,484 | 155.2 | 19,969 |
| 104 | 107.7 |  | 13,905 | 143.3 | 18,503 | 155.2 | 20,479 | 106.9 |  | 13,505 | 146.3 | 18,484 | 155.2 | 19,742 |
| 105 | 108.9 |  | 13,932 | 144.6 | 18,503 | 155.2 | 20,206 | 108.1 |  | 13,532 | 147.7 | 18,484 | 155.2 | 19,520 |

- Table values derived from HDC report (Jan 2004). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on cavitation or generator limit (added Feb 2018).

Table LWG-6. Lower Granite Dam a

| Project | LWG Units 1, 2b, 3 - With ESBS |  |  |  |  |  |  | LWG Units 1, 2b, 3 - No ESBS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs |  | MW | cfs | MW | cfs | MW | cfs |  | MW | cfs | MW | cfs |
| 85 | 69.9 | 11,938 |  | 116.2 | 19,863 | 140.9 | 25.5 | 65.7 | 10,897 |  | 120.6 | 20,010 | 140.9 | 24,226 |
| 86 | 70.6 | 11,922 |  | 118.5 | 20,007 | 142.8 | 25.5 | 66.4 | 10,882 |  | 123.0 | 20,155 | 142.8 | 24,243 |
| 87 | 71.4 | 11,906 |  | 120.8 | 20,146 | 144.6 | 25.5 | 67.2 | 10,868 |  | 125.4 | 20,296 | 144.6 | 24,258 |
| 88 | 72.2 | 11,890 |  | 123.1 | 20,282 | 146.5 | 25.5 | 67.9 | 10,853 |  | 127.8 | 20,434 | 146.5 | 24,272 |
| 89 | 73.0 | 11,875 |  | 125.4 | 20,415 | 148.3 | 25.5 | 68.6 | 10,839 |  | 130.2 | 20,568 | 148.3 | 24,283 |
| 90 | 73.7 | 11,859 |  | 127.7 | 20,544 | 150.2 | 25.5 | 69.3 | 10,826 |  | 132.6 | 20,698 | 150.2 | 24,292 |
| 91 | 74.6 | 11,849 |  | 128.1 | 20,346 | 151.5 | 25.4 | 70.2 | 10,817 |  | 133.0 | 20,500 | 151.5 | 24,217 |
| 92 | 75.5 | 11,839 |  | 128.5 | 20,152 | 152.8 | 25.3 | 71.0 | 10,808 |  | 133.3 | 20,305 | 152.8 | 24,139 |
| 93 | 76.3 | 11,829 |  | 128.8 | 19,963 | 154.0 | 25.2 | 71.8 | 10,799 |  | 133.7 | 20,115 | 154.0 | 24,059 |
| 94 | 77.2 | 11,818 |  | 129.2 | 19,777 | 155.2 | 25.1 | 72.6 | 10,790 |  | 134.1 | 19,929 | 155.2 | 23,973 |
| 95 | 78.1 | 11,808 |  | 129.5 | 19,596 | 155.2 | 24.8 | 73.4 | 10,781 |  | 134.4 | 19,747 | 155.2 | 23,646 |
| 96 | 79.1 | 11,825 |  | 129.7 | 19,385 | 155.2 | 24.5 | 74.4 | 10,797 |  | 134.6 | 19,536 | 155.2 | 23,322 |
| 97 | 80.2 | 11,841 |  | 129.8 | 19,179 | 155.2 | 24.1 | 75.4 | 10,813 |  | 134.7 | 19,329 | 155.2 | 23,004 |
| 98 | 81.2 | 11,857 |  | 130.0 | 18,978 | 155.2 | 23.8 | 76.4 | 10,827 |  | 134.9 | 19,126 | 155.2 | 22,694 |
| 99 | 82.3 | 11,872 |  | 130.1 | 18,780 | 155.2 | 23.5 | 77.4 | 10,842 |  | 135.0 | 18,928 | 155.2 | 22,390 |
| 100 | 83.3 | 11,887 |  | 130.3 | 18,586 | 155.2 | 23.2 | 78.3 | 10,855 |  | 135.2 | 18,734 | 155.2 | 22,093 |
| 101 | 84.2 | 11,890 |  | 132.0 | 18,637 | 155.2 | 22.8 | 79.2 | 10,858 |  | 137.0 | 18,785 | 155.2 | 21,784 |
| 102 | 85.1 | 11,892 |  | 133.7 | 18,687 | 155.2 | 22.5 | 80.0 | 10,860 |  | 138.8 | 18,836 | 155.2 | 21,482 |
| 103 | 86.0 | 11,895 |  | 135.4 | 18,736 | 155.2 | 22.2 | 80.9 | 10,863 |  | 140.6 | 18,885 | 155.2 | 21,186 |
| 104 | 86.9 | 11,897 |  | 137.2 | 18,784 | 155.2 | 21.9 | 81.7 | 10,865 |  | 142.4 | 18,934 | 155.2 | 20,897 |
| 105 | 87.8 | 11,899 |  | 138.9 | 18,830 | 155.2 | 21.6 | 82.5 | 10,867 |  | 144.2 | 18,981 | 155.2 | 20,615 |
|  | LWG Units 4, 5, 6 - With ESBS |  |  |  |  |  |  | LWG Units 4, 5, 6 - No ESBS |  |  |  |  |  |  |
| 85 | 83.9 |  | 13,761 | 107.2 | 17,586 | 142.5 | 24,793 | 85.1 |  | 13,602 | 116.0 | 18,546 | 142.5 | 23,969 |
| 86 | 85.0 |  | 13,769 | 108.9 | 17,652 | 144.3 | 24,810 | 86.1 |  | 13,600 | 117.9 | 18,616 | 144.3 | 23,986 |
| 87 | 86.1 |  | 13,777 | 110.7 | 17,717 | 146.1 | 24,825 | 87.2 |  | 13,597 | 119.8 | 18,685 | 146.1 | 24,001 |
| 88 | 87.1 |  | 13,784 | 112.4 | 17,780 | 147.9 | 24,838 | 88.2 |  | 13,595 | 121.7 | 18,751 | 147.9 | 24,013 |
| 89 | 88.2 |  | 13,791 | 114.2 | 17,841 | 149.7 | 24,849 | 89.2 |  | 13,592 | 123.5 | 18,816 | 149.7 | 24,024 |
| 90 | 89.3 |  | 13,798 | 115.9 | 17,900 | 151.4 | 24,857 | 90.3 |  | 13,589 | 125.4 | 18,879 | 151.4 | 24,032 |
| 91 | 90.3 |  | 13,778 | 117.1 | 17,878 | 152.8 | 24,721 | 91.4 |  | 13,598 | 126.8 | 18,856 | 152.8 | 23,946 |
| 92 | 91.2 |  | 13,759 | 118.4 | 17,857 | 154.1 | 24,583 | 92.5 |  | 13,607 | 128.1 | 18,834 | 154.1 | 23,857 |
| 93 | 92.1 |  | 13,740 | 119.6 | 17,836 | 155.2 | 24,425 | 93.7 |  | 13,615 | 129.4 | 18,812 | 155.2 | 23,747 |
| 94 | 93.1 |  | 13,722 | 120.8 | 17,815 | 155.2 | 24,112 | 94.8 |  | 13,623 | 130.8 | 18,791 | 155.2 | 23,676 |
| 95 | 94.0 |  | 13,703 | 122.0 | 17,795 | 155.2 | 23,675 | 95.9 |  | 13,630 | 132.1 | 18,769 | 155.2 | 23,011 |
| 96 | 95.1 |  | 13,707 | 122.6 | 17,676 | 155.2 | 23,372 | 96.9 |  | 13,620 | 132.7 | 18,645 | 155.2 | 21,828 |
| 97 | 96.1 |  | 13,711 | 123.1 | 17,560 | 155.2 | 23,076 | 97.9 |  | 13,609 | 133.3 | 18,523 | 155.2 | 21,557 |
| 98 | 97.2 |  | 13,714 | 123.7 | 17,446 | 155.2 | 22,786 | 98.9 |  | 13,599 | 133.9 | 18,403 | 155.2 | 21,292 |
| 99 | 98.3 |  | 13,717 | 124.2 | 17,335 | 155.2 | 22,502 | 99.9 |  | 13,589 | 134.5 | 18,285 | 155.2 | 21,032 |
| 100 | 99.4 |  | 13,720 | 124.8 | 17,225 | 155.2 | 22,224 | 100.9 |  | 13,579 | 135.0 | 18,170 | 155.2 | 21,620 |
| 101 | 100.4 |  | 13,724 | 126.0 | 17,227 | 155.2 | 21,941 | 101.9 |  | 13,579 | 136.4 | 18,172 | 155.2 | 21,325 |
| 102 | 101.4 |  | 13,728 | 127.3 | 17,229 | 155.2 | 21,665 | 102.9 |  | 13,580 | 137.8 | 18,174 | 155.2 | 21,036 |
| 103 | 102.5 |  | 13,731 | 128.6 | 17,230 | 155.2 | 21,394 | 104.0 |  | 13,580 | 139.1 | 18,175 | 155.2 | 20,753 |
| 104 | 103.5 |  | 13,735 | 129.8 | 17,232 | 155.2 | 21,128 | 105.0 |  | 13,581 | 140.5 | 18,177 | 155.2 | 20,477 |
| 105 | 104.5 |  | 13,739 | 131.1 | 17,233 | 155.2 | 20,868 | 106.0 |  | 13,581 | 141.9 | 18,179 | 155.2 | 20,206 |

- Table values derived from HDC report (Nov 2006). Flow (cfs) is calculated based on turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point, based on cavitation or generator limit (added Feb 2018).

- Unit 2 runner blades were hydraulically locked in April 2017 due to failed blade packing sleeves. As a result, Unit 2 is restricted to a smaller operating range of approximately 17-19 kcfs until the unit is repaired.