# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	18BON004 – PH1 Chiller Water Discharge

Date Submitted: 		May 22, 2018

Project: 			Bonneville Dam

Requester Name, Agency: 	Andrew Derugin, USACE BON

Final Action:			APPROVED 6/14/18

FPP Section: BON section 2.4.2.12 – Adult Facilities / Fish Passage Season / PH1

Justification for Change: When the air conditioning unit for PH1 is turned on, it discharges warm water into one of two tail log gate wells, 8A or 9B.  This water is warm, between 74 and 85° F.  When this water dumps into a gate well of a non-running unit, there is little mixing, and the water in the gate well is heated.  The gate wells of non-running units tend to hold fish, and the temperature stress likely kills them.  We propose the addition of language to the FPP stating that heated discharge water must discharge to a running unit when available.  A separate change form will be submitted to change unit priority, switching unit 9 (last place) with unit 2 (currently 5th).

Proposed Changes:  Add new section “f” to 2.4.2.12.:

2.4.2.12.f.  CAC1 Discharge.  Direct discharge from the PH1 air conditioning into the gate well of a running unit (8 or 9), when available.

Comments: (listed from oldest to newest)

6/14/18 FPOM Meeting: Conder asked what would happen if both units were down. Hausmann said that the water would have to be rerouted but this would take a lot of work. Conder suggests looking for another method of routing the water but is okay with this in the meantime. FPOM concurred.

Record of Final Action:  Approved at FPOM 6/14/18