# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	18LGS004 – Differentials

Date Submitted: 		December 20, 2017

Project: 			Little Goose Dam

Requester Name, Agency: 	Scott St. John, USACE LGS

Final Action:			APPROVED – January 11, 2018

FPP Section:

Chapter 4 – Little Goose Dam:

- 2.3.2.1. (Juvenile Passage Season – Forebay Area and Intakes)

- 2.3.2.2. (Juvenile Passage Season – ESBS, VBS, and Operating Gates)

Justification for Change: In order to measure differentials, coordination with operators and BPA is required to conduct proper measurement.  Previous verbiage was contradictory as the same process is required to properly measure “drawdown differentials” as “VBS head differentials”.  This change updates the process so that the project improves tracking of VBS differentials and also conducts all measurements during the same intervals.  Additionally, it will be imperative that VBS differentials are monitored as operating gates no longer need to be in the raised position (MOC 17LGS007) which could change VBS differential criteria in the future.

Proposed Change: [see below with edits to existing FPP in track changes]

2.3.2.1. Forebay Area and Intakes.

iv. Log drawdown differentials in bulkhead slots at least once a week  March 1 (2018 only*) - June 30 and biweekly (once every two weeks) for the remainder of the operating season.

2.3.2.2. ESBS, VBS, and Operating Gates.

xi.  Log VBS head differentials at least once per week  March 1 (2018 only*)–June 30 (more frequently if required) and biweekly (once every two weeks) for the remainder of the operating season. When a head differential of 1.5' is reached, the respective turbine unit should be operated at a reduced loading (≤ 110 MW) to minimize loading on the VBS and potential fish impingement until the VBS can be cleaned. Clean VBSs as soon as possible after a 1.5' head differential is reached.

Comments: FPOM 1/11/18: Added clarification that “biweekly” = “once every two weeks”.

Record of Final Action:  Approved at FPOM 1/11/18.