# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	18LWG002 – Updates for Units 1 and 2

Date Submitted: 		February 1, 2018

Project: 			LWG

Requester Name, Agency: 	Corps NWW

Final Action:			APPROVED 2/8/18

FPP Section:

Table LWG-5. Unit Priority Order.

Footnote to Table LWG-6. Turbine 1% Range for Units 1–3

Justification for Change:

Updates the FPP to reflect the current status of Unit 1 (restored to fully-adjustable Kaplan) and Unit 2 (fixed blades in April 2017):

- Revises the unit priority order to move Unit 1 to first priority and Unit 2 to last-on/second-to-last off to minimize starts/stops to the extent possible.

- Revises footnote to the 1% table to remove Unit 1 restriction and add Unit 2 restriction.

Proposed Change: [see following page for edits to existing FPP text in track changes]

Comments:

Record of Final Action:  	APPROVED at FPOM 2/8/18

Table LWG-5.  Lower Granite Dam Turbine Unit Priority Order.

| Season | Unit Priority Order |
| --- | --- |
| March 1 – December 15 Fish Passage Season | Start Units: 1, 3, 4–6 any order, then 2a Stop Units: 4–6 any order, 3, 2, 1 |
| December 16 – end of February Winter Maintenance Period | Any Order |

a. Unit 2 has fixed Kaplan blades (hydraulically locked) and operates in the upper 1% range. The priority order minimizes starts/stops and allows for the longest runtime once Unit 2 is started.

b. Stop units in reverse Start order except run Unit 2 as long as BPA load request and required spill can be met, and stop Unit 2 before Unit 1.

Table LWG-6. Turbine 1% Range for Units 1-3.

DELETE footnote for Unit 1 restriction and ADD footnote for Unit 2 restriction.

b. Unit 2 has hydraulically locked runner blades due to failed blade packing sleeves. As a result, Unit 2 is restricted to a smaller operating range of approximately 17-19 kcfs until the unit is repaired.