# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	19IHR004 – Unit Updates

Date Submitted: 		January 14, 2019

Project: 			Ice Harbor Dam

Requester Name, Agency: 	Corps NWW

Final Action:			APPROVED – 2/7/2019

FPP Section:  Table IHR-5 (Units 1-3 Range) and Table IHR-6 (Units 4-6 Range)

Justification for Change:

Updates the 2019 FPP with current status of IHR units:

- Unit 2 has a new runner design and is currently scheduled to return to service in early 2019. Index testing will be performed to determine the new 1% operating range. The FPP will be updated with those values when they’re available.

- Unit 3 will be out of service in 2019 to install new runner design (currently scheduled through early 2020);

- Unit 6 runner blades are hydraulically locked at 24°, which is the same angle as Unit 5 between peak efficiency and the upper 1% limit (approx. 13-14 kcfs). This was coordinated with FPOM at the December 2018 meeting.

Proposed Changes:  See following pages for edits to existing FPP text in track changes.

Comments:

Record of Final Action:   Approved at the FPOM FPP meeting on 2/7/2019.

Table IHR-5. Ice Harbor Dam Turbine Unit Power (MW) and Flow (cfs) at ±1% of Peak Turbine Efficiency (i.e., Lower and Upper Limits of 1% Range) and at Operating Limits. a

| Project | IHR Unit 1 - With STS |  |  |  |  |  | IHR Unit 1 - No STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 85 | 51.7 | 8,417 | 83.6 | 13,590 | 92.8 | 16,053 | 51.9 | 8,340 | 89.9 | 14,452 | 102.6 | 16,859 |
| 86 | 52.6 | 8,443 | 84.6 | 13,585 | 94.3 | 16,077 | 52.7 | 8,367 | 91.0 | 14,447 | 103.1 | 16,715 |
| 87 | 53.4 | 8,469 | 85.6 | 13,580 | 95.7 | 16,099 | 53.5 | 8,392 | 92.0 | 14,441 | 103.5 | 16,568 |
| 88 | 54.2 | 8,494 | 86.6 | 13,574 | 97.3 | 16,144 | 54.3 | 8,417 | 93.1 | 14,436 | 103.5 | 16,420 |
| 89 | 55.0 | 8,518 | 87.6 | 13,569 | 99.0 | 16,187 | 55.1 | 8,441 | 94.2 | 14,430 | 103.5 | 16,252 |
| 90 | 55.8 | 8,542 | 88.6 | 13,563 | 100.1 | 16,158 | 55.9 | 8,465 | 95.3 | 14,424 | 103.5 | 16,034 |
| 91 | 56.5 | 8,548 | 89.8 | 13,585 | 101.0 | 16,058 | 56.6 | 8,471 | 96.5 | 14,448 | 103.5 | 15,822 |
| 92 | 57.1 | 8,554 | 90.9 | 13,607 | 101.9 | 15,960 | 57.3 | 8,477 | 97.8 | 14,471 | 103.5 | 15,614 |
| 93 | 57.8 | 8,559 | 92.1 | 13,628 | 102.8 | 15,864 | 58.0 | 8,482 | 99.0 | 14,494 | 103.5 | 15,411 |
| 94 | 58.5 | 8,565 | 93.2 | 13,649 | 103.5 | 15,769 | 58.6 | 8,488 | 100.3 | 14,516 | 103.5 | 15,213 |
| 95 | 59.2 | 8,570 | 94.4 | 13,669 | 103.5 | 15,675 | 59.3 | 8,493 | 101.5 | 14,537 | 103.5 | 15,019 |
| 96 | 59.9 | 8,589 | 95.3 | 13,662 | 103.5 | 15,425 | 60.1 | 8,511 | 102.5 | 14,530 | 103.5 | 14,845 |
| 97 | 60.7 | 8,607 | 96.3 | 13,655 | 103.5 | 15,180 | 60.8 | 8,529 | Operating Limit b 14,676 |  | 103.5 | 14,676 |
| 98 | 61.5 | 8,624 | 97.3 | 13,648 | 103.5 | 14,941 | 61.6 | 8,546 | Operating Limit b 14,509 |  | 103.5 | 14,509 |
| 99 | 62.2 | 8,641 | 98.2 | 13,641 | 103.5 | 14,708 | 62.4 | 8,563 | Operating Limit b 14,347 |  | 103.5 | 14,347 |
| 100 | 63.0 | 8,658 | 99.2 | 13,634 | 103.5 | 14,481 | 63.1 | 8,580 | Operating Limit b |  | 103.5 | 14,187 |
| 101 | 64.0 | 8,707 | 99.9 | 13,590 | 103.5 | 14,318 | 64.1 | 8,629 | Operating Limit b |  | 103.5 | 14,037 |
| 102 | 65.0 | 8,756 | 100.6 | 13,547 | 103.5 | 14,158 | 65.2 | 8,677 | Operating Limit b |  | 103.5 | 13,890 |
| 103 | 66.0 | 8,804 | 101.3 | 13,505 | 103.5 | 14,001 | 66.2 | 8,725 | Operating Limit b |  | 103.5 | 13,746 |
| 104 | 67.0 | 8,850 | 102.0 | 13,463 | 103.5 | 13,847 | 67.2 | 8,771 | Operating Limit b |  | 103.5 | 13,605 |
| 105 | 68.0 | 8,896 | 102.6 | 13,422 | 103.5 | 13,697 | 68.2 | 8,816 | Operating Limit b |  | 103.5 | 13,466 |
|  | IHR Unit 2 c - With STS |  |  |  |  |  | IHR Unit 2 c - No STS |  |  |  |  |  |
| 85 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 86 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 87 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 88 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 89 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 90 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 91 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 92 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 93 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 94 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 95 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 96 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 97 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 98 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 99 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 100 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 101 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 102 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 103 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 104 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |
| 105 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |

| Project | IHR Unit 3 d - With STS |  |  |  |  |  | IHR Unit 3 d - No STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 85 |  |  |  |  |  |  |  |  |  |  |  |  |
| 86 |  |  |  |  |  |  |  |  |  |  |  |  |
| 87 |  |  |  |  |  |  |  |  |  |  |  |  |
| 88 |  |  |  |  |  |  |  |  |  |  |  |  |
| 89 |  |  |  |  |  |  |  |  |  |  |  |  |
| 90 |  |  |  |  |  |  |  |  |  |  |  |  |
| 91 |  |  |  |  |  |  |  |  |  |  |  |  |
| 92 |  |  |  |  |  |  |  |  |  |  |  |  |
| 93 |  |  |  |  |  |  |  |  |  |  |  |  |
| 94 |  |  |  |  |  |  |  |  |  |  |  |  |
| 95 |  |  |  |  |  |  |  |  |  |  |  |  |
| 96 |  |  |  |  |  |  |  |  |  |  |  |  |
| 97 |  |  |  |  |  |  |  |  |  |  |  |  |
| 98 |  |  |  |  |  |  |  |  |  |  |  |  |
| 99 |  |  |  |  |  |  |  |  |  |  |  |  |
| 100 |  |  |  |  |  |  |  |  |  |  |  |  |
| 101 |  |  |  |  |  |  |  |  |  |  |  |  |
| 102 |  |  |  |  |  |  |  |  |  |  |  |  |
| 103 |  |  |  |  |  |  |  |  |  |  |  |  |
| 104 |  |  |  |  |  |  |  |  |  |  |  |  |
| 105 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IHR Units 4, 5e, 6e - With STS |  |  |  |  |  | IHR Units 4, 5e, 6e - No STS |  |  |  |  |  |
| 85 | 58.9 | 9,369 | 93.1 | 14,810 | 121.8 | 20,745 | 62.0 | 9,745 | 110.7 | 17,413 | 121.8 | 19,401 |
| 86 | 59.7 | 9,380 | 94.4 | 14,824 | 122.7 | 20,569 | 62.8 | 9,756 | 112.3 | 17,430 | 122.7 | 19,283 |
| 87 | 60.6 | 9,390 | 95.7 | 14,838 | 123.4 | 20,392 | 63.7 | 9,767 | 113.8 | 17,447 | 123.4 | 19,162 |
| 88 | 61.4 | 9,400 | 97.0 | 14,851 | 124.2 | 20,212 | 64.5 | 9,777 | 115.3 | 17,462 | 124.2 | 19,039 |
| 89 | 62.2 | 9,410 | 98.2 | 14,864 | 124.9 | 20,034 | 65.4 | 9,787 | 116.8 | 17,477 | 124.9 | 18,905 |
| 90 | 63.0 | 9,419 | 99.5 | 14,876 | 125.6 | 19,747 | 66.3 | 9,797 | 118.3 | 17,492 | 125.6 | 18,752 |
| 91 | 63.7 | 9,416 | 100.7 | 14,885 | 126.2 | 19,569 | 67.0 | 9,794 | 119.8 | 17,503 | 126.2 | 18,599 |
| 92 | 64.5 | 9,414 | 102.0 | 14,895 | 126.9 | 19,389 | 67.8 | 9,792 | 121.3 | 17,515 | 126.9 | 18,445 |
| 93 | 65.2 | 9,411 | 103.2 | 14,904 | 127.2 | 19,159 | 68.6 | 9,789 | 122.7 | 17,525 | 127.2 | 18,242 |
| 94 | 65.9 | 9,409 | 104.5 | 14,912 | 127.2 | 18,893 | 69.3 | 9,787 | 124.2 | 17,535 | 127.2 | 18,004 |
| 95 | 66.6 | 9,406 | 105.7 | 14,921 | 127.2 | 18,633 | 70.1 | 9,784 | 125.7 | 17,545 | 127.2 | 17,771 |
| 96 | 67.5 | 9,416 | 106.7 | 14,892 | 127.2 | 18,396 | 70.9 | 9,794 | 126.8 | 17,512 | 127.2 | 17,560 |
| 97 | 68.3 | 9,425 | 107.7 | 14,864 | 127.2 | 18,165 | 71.8 | 9,804 | Operating Limit b |  | 127.2 | 17,353 |
| 98 | 69.1 | 9,434 | 108.6 | 14,836 | 127.2 | 17,938 | 72.7 | 9,813 | Operating Limit b |  | 127.2 | 17,150 |
| 99 | 69.9 | 9,442 | 109.6 | 14,809 | 127.2 | 17,717 | 73.5 | 9,822 | Operating Limit b |  | 127.2 | 16,952 |
| 100 | 70.7 | 9,451 | 110.6 | 14,782 | 127.2 | 17,499 | 74.4 | 9,831 | Operating Limit b |  | 127.2 | 16,757 |
| 101 | 71.4 | 9,446 | 112.9 | 14,939 | 127.2 | 17,251 | 75.1 | 9,825 | Operating Limit b |  | 127.2 | 16,573 |
| 102 | 72.0 | 9,441 | 115.1 | 15,093 | 127.2 | 17,009 | 75.7 | 9,820 | Operating Limit b |  | 127.2 | 16,393 |
| 103 | 72.7 | 9,436 | 117.4 | 15,244 | 127.2 | 16,771 | 76.4 | 9,815 | Operating Limit b |  | 127.2 | 16,216 |
| 104 | 73.3 | 9,431 | 119.7 | 15,392 | 127.2 | 16,539 | 77.1 | 9,810 | Operating Limit b |  | 127.2 | 16,042 |
| 105 | 74.0 | 9,426 | 121.9 | 15,538 | 127.2 | 16,312 | 77.8 | 9,805 | Operating Limit b |  | 127.2 | 15,872 |

- Table values for 1% upper and lower limits derived from March 2007 HDC report. Flow (cfs) is calculated as a function of turbine efficiency, project head, and power output (MW).

- “Operating Limit” is the maximum safe operating point based on cavitation or generator limit (added Feb 2018). Units operating without STSs (e.g., during winter maintenance period) at head ≥ 97 ft are restricted by the Operating Limit.

- Unit 2 was rebuilt with a new runner design and is scheduled to be returned to service in early 2019.  Table will be revised pending index tests.

- Unit 3 is out of service in 2019 for turbine replacement,  currently scheduled through early 2020. Table will be revised after completion of U3 turbine replacement and index testing.

- Units 5 and 6 have fixed blades and a restricted operating range of approximately 13-14 kcfs (from 2017 U5 abbreviated index test). These units will have a restricted operating range until the blade seals are repaired/replaced.