# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	19LMN003 – Unit Updates

Date Submitted: 		1/14/2019

Project: 			Lower Monumental Dam

Requester Name, Agency: 	Ann Setter, Corps NWW

Final Action:			APPROVED – 2/7/2019

FPP Section:  LMN section 4.1 (Unit Priority Order) and Tables LMN-5 and LMN-6

Justification for Change:

Updates the 2019 FPP with the current status of LMN turbine units with locked blades. Currently, only Unit 2 is still hydraulically locked and has a restricted operating range. Units 3 and 4 had their blade seals replaced in 2018 and are no longer locked at a fixed angle (can be operated in full 1%). Therefore, this change form removes language regarding Units 3 and 4 restrictions where necessary.

Proposed Changes:  	See following pages for edits to existing FPP text in track changes.

Comments:

2/7/19 FPP Meeting: Setter provided an update that Unit 3 was still not repaired but is scheduled to be before spill starts. FPOM approved this change form, recognizing it may change in-season. If there is a delay in Unit 3 repair that requires it to operate as a fixed blade unit, it will be moved to last-on/first-off priority, like in 2018.

Record of Final Action:   Approved at the FPOM FPP meeting on 2/7/2019.

- 4. 	TURBINE UNIT OPERATION & MAINTENANCE

- 4.1. 	Turbine Unit Priority Order.

- 4.1.1. From March 1 through November 30, turbine units will be operated in the order of priority defined in Table LMN-5 in order to enhance adult and juvenile fish passage. If a turbine unit is out of service for maintenance or repair, the next unit in the priority order shall be operated.

- 4.1.2. Unit priority order may be coordinated differently to allow for fish research, construction, or project maintenance activities.

- 4.1.3. Unit 1 provides the best fish passage conditions by eliminating the eddy at the juvenile fish loading dock and providing attraction flow to the North adult fish ladder. Therefore, the default priority order for fish passage is Units 1–6 (in order from north to south). However, due to blade seal failures on Unit 2, the blades were hydraulically locked at a fixed angle, which restricts the unit to a narrow operating range (see 1% range tables in section 4.2). To avoid excessive wear and tear from repeated starts/stops, Unit 2 is operated last-on/last-off in the priority order for all flow conditions until repairs are completed. When Unit 1 is not available, Unit 2 will be the first priority unit for fish passage.

Table LMN-5. Lower Monumental Dam Turbine Unit Priority Order.

| Season | Unit Priority Order |
| --- | --- |
| March 1 – November 30 Fish Passage Season | DEFAULT 1, 2, 3, 4, 5, 6 MODIFIED ORDER for Fixed-Blade Units* Start-up (U1 available): 1, 3, 4, 5, 6, 2* Start-up (U1 not available): 2*, 3, 4, 5, 6 Shutdown: 6, 5, 4, 3, 2*, 1 |
| December 1 – End of February Winter Maintenance Period | Any Order |

*Units that have hydraulically locked runner blades will be operated in a modified priority order to minimize starts/stops. As of Feb 2019, Unit 2 has hydraulically locked blades. When Unit 1 is unavailable, Unit 2 will be first priority for fish passage. When the blade seals are replaced, the unit will resume operating in its default order.

Footnotes to Table LMN-6. Lower Monumental Dam Turbine Unit 1% Range.

- Table values for 1% upper and lower limits derived from HDC report (July 2003). Flow (cfs) is calculated as a function of turbine efficiency, head, and power output (MW). “Operating Limit” is the maximum safe operating point based on cavitation or generator limit (added Feb 2018).

- Unit 2 runner blades are hydraulically locked due to failed blade seals (Sep 2017) and is restricted to the lower 1% (~11-13 kcfs).