# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	19MCN004 – Unit 6 Fixed Blade Operating Range

Date Submitted:		February 12, 2019

Project:			McNary Dam

Requester Name, Agency:	A. Setter, Corps

Final Action:			APPROVED – 2/14/2019

FPP Section:  Table MCN-6. Turbine Unit Operating Range.

Justification for Change:   McNary Unit 6 runner blades were fixed at 22° to prevent oil leaks. Based on index testing in January 2019, the restricted operating range is approximately 47-67 MW, which equates to a turbine discharge of ~10.2-11.6 kcfs. This change form adds that info as a footnote to Table MCN-6.

Proposed Change:

Add footnote to Table MCN-6 (see next page in track changes).

Comments:

Record of Final Action:  Approved at FPOM 2/14/19

Table MCN-6. McNary Dam Turbine Unit Power (MW) and Flow (cfs) at ±1% of Peak Turbine Efficiency (Lower and Upper Limits of 1% Range) and Operating Limits. a, b

| Project | With ESBS |  |  |  |  |  | No ESBS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 62 | 34.5 | 7,951 | 49.7 | 11,454 | 68.0 | 16,311 | 34.7 | 7754 | 50.8 | 11,346 | 68.0 | 15,710 |
| 63 | 35.2 | 7,963 | 51.0 | 11,552 | 69.6 | 16,399 | 35.4 | 7765 | 52.1 | 11,444 | 69.6 | 15,793 |
| 64 | 35.8 | 7,974 | 52.3 | 11,646 | 71.2 | 16,486 | 36.0 | 7776 | 53.5 | 11,537 | 71.2 | 15,875 |
| 65 | 36.5 | 7,984 | 53.7 | 11,736 | 72.8 | 16,571 | 36.7 | 7,786 | 54.8 | 11,627 | 72.8 | 15,955 |
| 66 | 37.0 | 7,959 | 55.2 | 11,869 | 74.1 | 16,574 | 37.2 | 7,762 | 56.3 | 11,759 | 74.1 | 15,945 |
| 67 | 37.5 | 7,934 | 56.7 | 11,997 | 75.3 | 16,574 | 37.7 | 7,739 | 57.9 | 11,887 | 75.3 | 15,933 |
| 68 | 38.0 | 7,911 | 58.2 | 12,121 | 76.6 | 16,572 | 38.2 | 7,716 | 59.4 | 12,009 | 76.6 | 15,919 |
| 69 | 38.5 | 7,887 | 59.7 | 12,240 | 77.8 | 16,567 | 38.7 | 7,694 | 60.9 | 12,128 | 77.8 | 15,903 |
| 70 | 39.0 | 7,864 | 61.2 | 12,355 | 79.0 | 16,560 | 39.2 | 7,671 | 62.5 | 12,243 | 79.0 | 15,884 |
| 71 | 39.6 | 7,874 | 62.1 | 12,355 | 79.7 | 16,433 | 39.8 | 7,681 | 63.4 | 12,243 | 79.7 | 15,782 |
| 72 | 40.2 | 7,883 | 63.1 | 12,354 | 80.4 | 16,303 | 40.4 | 7,691 | 64.4 | 12,242 | 80.4 | 15,676 |
| 73 | 40.9 | 7,892 | 64.0 | 12,353 | 81.0 | 16,169 | 41.1 | 7,699 | 65.3 | 12,241 | 81.0 | 15,567 |
| 74 | 41.5 | 7,901 | 64.9 | 12,351 | 81.6 | 16,033 | 41.7 | 7,708 | 66.3 | 12,240 | 81.3 | 15,455 |
| 75 | 42.2 | 7,909 | 65.8 | 12,350 | 82.2 | 15,893 | 42.4 | 7,716 | 67.2 | 12,239 | 81.3 | 15,340 |
| 76 | 42.8 | 7,907 | 66.4 | 12,282 | 82.5 | 15,705 | 43.0 | 7,714 | 67.9 | 12,172 | 81.3 | 15,161 |
| 77 | 43.4 | 7,905 | 67.1 | 12,216 | 82.8 | 15,513 | 43.6 | 7,713 | 68.5 | 12,107 | 81.3 | 14,979 |
| 78 | 44.0 | 7,903 | 67.7 | 12,151 | 83.1 | 15,319 | 44.2 | 7,711 | 69.1 | 12,044 | 81.3 | 14,795 |
| 79 | 44.6 | 7,900 | 68.3 | 12,088 | 83.3 | 15,122 | 44.8 | 7,709 | 69.7 | 11,981 | 81.3 | 14,608 |
| 80 | 45.2 | 7,897 | 68.9 | 12,026 | 83.4 | 14,922 | 45.5 | 7,706 | 70.3 | 11,920 | 81.3 | 14,418 |
| 81 | 45.9 | 7,911 | 70.0 | 12,067 | 83.7 | 14,747 | 46.1 | 7,720 | 71.5 | 11,961 | 81.3 | 14,256 |
| 82 | 46.5 | 7,925 | 71.1 | 12,106 | 83.8 | 14,569 | 46.8 | 7,734 | 72.6 | 12,000 | 81.3 | 14,091 |
| 83 | 47.2 | 7,939 | 72.2 | 12,145 | 84.0 | 14,389 | 47.4 | 7,747 | 73.7 | 12,038 | 81.3 | 13,924 |
| 84 | 47.9 | 7,952 | 73.3 | 12,182 | 84.1 | 14,206 | 48.1 | 7,759 | 74.9 | 12,076 | 81.3 | 13,754 |
| 85 | 48.5 | 7,964 | 74.4 | 12,219 | 84.2 | 14,020 | 48.8 | 7,772 | 76.0 | 12,112 | 81.3 | 13,582 |
| 86 | 49.2 | 7,987 | 75.1 | 12,179 | 84.0 | 13,806 | 49.5 | 7,794 | 76.7 | 12,073 | 81.3 | 13,373 |
| 87 | 50.0 | 8,008 | 75.7 | 12,140 | 83.8 | 13,588 | 50.2 | 7,815 | 77.3 | 12,034 | 81.3 | 13,161 |

- Table values for 1% upper and lower limits derived from HDC report (Mar 1999; updated Jan 2005). Flow (cfs) is calculated as a function of turbine efficiency, project head, and power output (MW). “Operating Limit” is the maximum safe operating point based on cavitation or generator limit (added Feb 2018).

- Unit 6 has a restricted operating range of approximately 10.2–11.6 kcfs (based on Jan 2019 index test results) due to blades that have been fixed at 22° to prevent oil leaks. This restricted operating range will be in effect until the unit is restored to a fully-adjustable Kaplan.