# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:  	20JDA002 – Operating Range Table for Locked-Blade Units

Date Submitted:		5 February 2020

Project:			John Day Dam

Requester Name, Agency:	Lisa Wright, Corps RCC

Final Action:

FPP Section:

Table JDA-7. Turbine Unit Operating Ranges.

Justification for Change:

Need to add a table of turbine operating ranges for units with locked runner blades. Until now, the range has been estimated in a footnote to the table. Adding a separate table defines the operating limits over a range of heads.

Proposed Change:

See next page with edits to existing Table JDA-7 in track changes.

Comments:

Record of Final Action:

Table JDA-7-A. Operating Range Values for John Day Turbine Units 4, 8, 9, 11, 12, and 14 with Locked Runner Blades

(Non-Adjustable). a

| Project Head (feet) | Unit 4 w/ Blades Locked at ~29.1° (May 2016) |  |  |  |  |  |  |  | Unit 8 w/ Blades Locked at ~29.4° (March 2017) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | With STS |  |  |  | No STS |  |  |  | With STS |  |  |  | No STS |  |  |  |
|  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  |
|  | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 80 | 103.1 | 18,040 | 108.0 | 18,909 | 103.5 | 17,912 | 108.5 | 18,771 | 105.7 | 18,499 | 109.4 | 19,157 | 106.1 | 18,366 | 109.9 | 19,017 |
| 81 | 104.4 | 18,019 | 109.3 | 18,857 | 104.9 | 17,892 | 109.7 | 18,720 | 107.1 | 18,478 | 110.7 | 19,105 | 107.5 | 18,345 | 111.2 | 18,966 |
| 82 | 105.8 | 17,998 | 110.5 | 18,806 | 106.3 | 17,871 | 111.0 | 18,670 | 108.5 | 18,456 | 112.0 | 19,054 | 108.9 | 18,323 | 112.5 | 18,915 |
| 83 | 107.1 | 17,977 | 111.8 | 18,756 | 107.6 | 17,850 | 112.3 | 18,621 | 109.9 | 18,434 | 113.3 | 19,003 | 110.3 | 18,302 | 113.7 | 18,865 |
| 84 | 108.5 | 17,955 | 113.0 | 18,706 | 109.0 | 17,829 | 113.5 | 18,572 | 111.3 | 18,412 | 114.5 | 18,952 | 111.7 | 18,280 | 115.0 | 18,815 |
| 85 | 109.9 | 17,933 | 114.3 | 18,657 | 110.4 | 17,808 | 114.8 | 18,523 | 112.7 | 18,389 | 115.8 | 18,902 | 113.1 | 18,259 | 116.3 | 18,766 |
| 86 | 111.5 | 17,969 | 115.8 | 18,662 | 112.0 | 17,843 | 116.3 | 18,528 | 114.4 | 18,426 | 117.4 | 18,907 | 114.9 | 18,295 | 117.9 | 18,771 |
| 87 | 113.2 | 18,003 | 117.5 | 18,687 | 113.7 | 17,877 | 118.0 | 18,554 | 116.1 | 18,461 | 119.1 | 18,936 | 116.6 | 18,330 | 119.6 | 18,800 |
| 88 | 114.9 | 18,036 | 119.2 | 18,711 | 115.4 | 17,910 | 119.7 | 18,578 | 117.8 | 18,494 | 120.8 | 18,964 | 118.3 | 18,364 | 121.3 | 18,828 |
| 89 | 116.5 | 18,067 | 120.8 | 18,734 | 117.1 | 17,942 | 121.4 | 18,601 | 119.5 | 18,527 | 122.5 | 18,990 | 120.0 | 18,396 | 123.0 | 18,854 |
| 90 | 118.2 | 18,097 | 122.0 | 18,674 | 118.7 | 17,972 | 122.5 | 18,542 | 121.2 | 18,557 | 123.6 | 18,920 | 121.7 | 18,427 | 124.1 | 18,785 |
| 91 | 119.6 | 18,096 | 123.7 | 18,703 | 120.2 | 17,971 | 124.2 | 18,571 | 122.7 | 18,556 | 125.3 | 18,949 | 123.2 | 18,426 | 125.8 | 18,814 |
| 92 | 121.1 | 18,094 | 125.3 | 18,731 | 121.6 | 17,969 | 125.9 | 18,598 | 124.2 | 18,554 | 127.0 | 18,977 | 124.7 | 18,424 | 127.5 | 18,842 |
| 93 | 122.5 | 18,092 | 127.0 | 18,757 | 123.1 | 17,967 | 127.6 | 18,625 | 125.6 | 18,552 | 128.7 | 19,004 | 126.2 | 18,422 | 129.2 | 18,869 |
| 94 | 124.0 | 18,089 | 128.7 | 18,783 | 124.5 | 17,965 | 129.3 | 18,651 | 127.1 | 18,549 | 130.4 | 19,030 | 127.7 | 18,420 | 131.0 | 18,895 |
| 95 | 125.4 | 18,086 | 130.4 | 18,807 | 126.0 | 17,962 | 131.0 | 18,675 | 128.6 | 18,546 | 132.1 | 19,055 | 129.2 | 18,417 | 132.7 | 18,920 |
| 96 | 126.9 | 18,100 | 132.0 | 18,821 | 127.5 | 17,976 | 132.5 | 18,689 | 130.1 | 18,561 | 133.7 | 19,069 | 130.7 | 18,432 | 134.3 | 18,934 |
| 97 | 128.4 | 18,114 | 133.5 | 18,834 | 129.0 | 17,990 | 134.1 | 18,702 | 131.7 | 18,574 | 135.3 | 19,082 | 132.3 | 18,445 | 135.8 | 18,947 |
| 98 | 129.9 | 18,127 | 135.1 | 18,846 | 130.5 | 18,003 | 135.7 | 18,714 | 133.2 | 18,588 | 136.9 | 19,094 | 133.8 | 18,459 | 137.4 | 18,959 |
| 99 | 131.4 | 18,139 | 136.6 | 18,858 | 132.0 | 18,015 | 137.2 | 18,726 | 134.8 | 18,600 | 138.4 | 19,106 | 135.4 | 18,471 | 139.0 | 18,971 |
| 100 | 132.9 | 18,151 | 138.2 | 18,869 | 133.5 | 18,027 | 138.8 | 18,737 | 136.3 | 18,612 | 140.0 | 19,117 | 136.9 | 18,483 | 140.6 | 18,983 |
| 101 | 134.2 | 18,128 | 139.7 | 18,868 | 134.8 | 18,004 | 140.3 | 18,737 | 137.6 | 18,589 | 141.5 | 19,117 | 138.2 | 18,460 | 142.1 | 18,982 |
| 102 | 135.4 | 18,105 | 141.1 | 18,868 | 136.0 | 17,982 | 141.7 | 18,736 | 138.9 | 18,565 | 143.0 | 19,116 | 139.5 | 18,437 | 143.6 | 18,982 |
| 103 | 136.7 | 18,082 | 142.6 | 18,866 | 137.3 | 17,959 | 143.2 | 18,735 | 140.2 | 18,542 | 144.5 | 19,115 | 140.8 | 18,414 | 145.1 | 18,981 |
| 104 | 137.9 | 18,060 | 144.1 | 18,865 | 138.5 | 17,937 | 144.7 | 18,734 | 141.4 | 18,519 | 146.0 | 19,113 | 142.0 | 18,391 | 146.6 | 18,979 |
| 105 | 139.2 | 18,038 | 145.6 | 18,864 | 139.8 | 17,915 | 146.2 | 18,732 | 142.7 | 18,496 | 147.5 | 19,112 | 143.3 | 18,369 | 148.1 | 18,978 |
| 106 | 140.0 | 17,965 | 146.9 | 18,846 | 140.7 | 17,843 | 147.5 | 18,715 | 143.6 | 18,422 | 148.8 | 19,094 | 144.2 | 18,295 | 149.5 | 18,960 |
| 107 | 140.9 | 17,893 | 148.2 | 18,828 | 141.5 | 17,772 | 148.9 | 18,697 | 144.5 | 18,348 | 150.2 | 19,076 | 145.1 | 18,222 | 150.8 | 18,942 |
| 108 | 141.7 | 17,822 | 149.6 | 18,810 | 142.4 | 17,702 | 150.2 | 18,680 | 145.3 | 18,276 | 151.6 | 19,058 | 146.0 | 18,150 | 152.2 | 18,925 |
| 109 | 142.6 | 17,753 | 150.9 | 18,792 | 143.2 | 17,633 | 151.6 | 18,662 | 146.2 | 18,205 | 152.9 | 19,040 | 146.8 | 18,080 | 153.6 | 18,907 |
| 110 | 143.4 | 17,685 | 152.3 | 18,775 | 144.1 | 17,566 | 152.9 | 18,645 | 147.1 | 18,135 | 154.3 | 19,022 | 147.7 | 18,010 | 154.9 | 18,889 |

| Project Head (feet) | Unit 9 w/ Blades Locked at ~29.0° (Sep 2015) |  |  |  |  |  |  |  | Unit 11 w/ Blades Locked at ~29.9° (April 2012) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | With STS |  |  |  | No STS |  |  |  | With STS |  |  |  | No STS |  |  |  |
|  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  |
|  | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 80 | 102.4 | 17,813 | 107.3 | 18,665 | 102.8 | 17,688 | 107.7 | 18,531 | 106.1 | 18,487 | 111.2 | 19,368 | 106.6 | 18,354 | 111.6 | 19,226 |
| 81 | 103.7 | 17,792 | 108.5 | 18,615 | 104.2 | 17,668 | 109.0 | 18,481 | 107.4 | 18,451 | 112.4 | 19,307 | 107.9 | 18,319 | 112.9 | 19,166 |
| 82 | 105.1 | 17,771 | 109.7 | 18,564 | 105.5 | 17,648 | 110.2 | 18,432 | 108.7 | 18,416 | 113.6 | 19,246 | 109.2 | 18,285 | 114.1 | 19,106 |
| 83 | 106.4 | 17,750 | 111.0 | 18,515 | 106.9 | 17,627 | 111.5 | 18,383 | 110.1 | 18,381 | 114.9 | 19,187 | 110.5 | 18,251 | 115.4 | 19,047 |
| 84 | 107.8 | 17,729 | 112.2 | 18,466 | 108.2 | 17,607 | 112.7 | 18,335 | 111.4 | 18,346 | 116.1 | 19,128 | 111.9 | 18,216 | 116.6 | 18,990 |
| 85 | 109.1 | 17,708 | 113.5 | 18,418 | 109.6 | 17,586 | 114.0 | 18,287 | 112.7 | 18,312 | 117.4 | 19,070 | 113.2 | 18,182 | 117.9 | 18,932 |
| 86 | 110.8 | 17,743 | 115.0 | 18,423 | 111.3 | 17,621 | 115.5 | 18,293 | 114.4 | 18,348 | 118.9 | 19,071 | 114.9 | 18,219 | 119.4 | 18,933 |
| 87 | 112.4 | 17,777 | 116.7 | 18,448 | 112.9 | 17,655 | 117.2 | 18,318 | 116.1 | 18,383 | 120.6 | 19,096 | 116.6 | 18,253 | 121.1 | 18,959 |
| 88 | 114.1 | 17,810 | 118.3 | 18,472 | 114.6 | 17,688 | 118.8 | 18,342 | 117.8 | 18,416 | 122.3 | 19,120 | 118.3 | 18,287 | 122.8 | 18,983 |
| 89 | 115.7 | 17,841 | 120.0 | 18,494 | 116.3 | 17,719 | 120.5 | 18,365 | 119.5 | 18,448 | 124.0 | 19,143 | 120.1 | 18,319 | 124.6 | 19,006 |
| 90 | 117.4 | 17,871 | 121.1 | 18,435 | 117.9 | 17,749 | 121.6 | 18,306 | 121.2 | 18,478 | 125.1 | 19,067 | 121.8 | 18,349 | 125.6 | 18,931 |
| 91 | 118.8 | 17,869 | 122.8 | 18,464 | 119.4 | 17,748 | 123.3 | 18,335 | 122.7 | 18,479 | 126.8 | 19,097 | 123.3 | 18,350 | 127.4 | 18,961 |
| 92 | 120.3 | 17,868 | 124.5 | 18,491 | 120.8 | 17,746 | 125.0 | 18,363 | 124.2 | 18,479 | 128.6 | 19,125 | 124.8 | 18,350 | 129.1 | 18,989 |
| 93 | 121.7 | 17,866 | 126.1 | 18,518 | 122.2 | 17,744 | 126.7 | 18,389 | 125.7 | 18,479 | 130.3 | 19,153 | 126.3 | 18,350 | 130.8 | 19,017 |
| 94 | 123.1 | 17,863 | 127.8 | 18,543 | 123.7 | 17,742 | 128.4 | 18,415 | 127.2 | 18,478 | 132.0 | 19,179 | 127.8 | 18,350 | 132.6 | 19,043 |
| 95 | 124.5 | 17,861 | 129.5 | 18,568 | 125.1 | 17,740 | 130.0 | 18,439 | 128.7 | 18,477 | 133.8 | 19,205 | 129.3 | 18,349 | 134.3 | 19,069 |
| 96 | 126.0 | 17,874 | 131.0 | 18,581 | 126.6 | 17,754 | 131.6 | 18,452 | 130.3 | 18,485 | 135.4 | 19,211 | 130.8 | 18,358 | 135.9 | 19,075 |
| 97 | 127.5 | 17,888 | 132.6 | 18,594 | 128.1 | 17,767 | 133.1 | 18,465 | 131.8 | 18,493 | 137.0 | 19,217 | 132.4 | 18,365 | 137.5 | 19,081 |
| 98 | 129.0 | 17,900 | 134.1 | 18,606 | 129.6 | 17,780 | 134.7 | 18,477 | 133.4 | 18,500 | 138.6 | 19,222 | 134.0 | 18,373 | 139.2 | 19,087 |
| 99 | 130.5 | 17,913 | 135.7 | 18,618 | 131.1 | 17,792 | 136.2 | 18,489 | 134.9 | 18,506 | 140.2 | 19,227 | 135.5 | 18,379 | 140.8 | 19,092 |
| 100 | 132.0 | 17,924 | 137.2 | 18,629 | 132.6 | 17,804 | 137.8 | 18,500 | 136.5 | 18,512 | 141.8 | 19,231 | 137.1 | 18,385 | 142.4 | 19,096 |
| 101 | 133.3 | 17,902 | 138.7 | 18,628 | 133.9 | 17,781 | 139.3 | 18,500 | 137.8 | 18,490 | 143.4 | 19,246 | 138.4 | 18,364 | 144.0 | 19,111 |
| 102 | 134.5 | 17,879 | 140.1 | 18,627 | 135.1 | 17,759 | 140.7 | 18,499 | 139.0 | 18,469 | 145.0 | 19,260 | 139.6 | 18,342 | 145.6 | 19,125 |
| 103 | 135.7 | 17,857 | 141.6 | 18,626 | 136.3 | 17,737 | 142.2 | 18,498 | 140.3 | 18,447 | 146.6 | 19,273 | 140.9 | 18,321 | 147.2 | 19,138 |
| 104 | 137.0 | 17,835 | 143.1 | 18,625 | 137.6 | 17,716 | 143.7 | 18,497 | 141.6 | 18,426 | 148.2 | 19,287 | 142.2 | 18,300 | 148.8 | 19,152 |
| 105 | 138.2 | 17,813 | 144.5 | 18,624 | 138.8 | 17,694 | 145.1 | 18,496 | 142.8 | 18,405 | 149.8 | 19,299 | 143.4 | 18,279 | 150.4 | 19,164 |
| 106 | 139.1 | 17,741 | 145.8 | 18,606 | 139.7 | 17,623 | 146.5 | 18,479 | 143.6 | 18,327 | 151.1 | 19,283 | 144.2 | 18,201 | 151.7 | 19,148 |
| 107 | 139.9 | 17,670 | 147.2 | 18,588 | 140.5 | 17,552 | 147.8 | 18,461 | 144.4 | 18,249 | 152.5 | 19,267 | 145.1 | 18,125 | 153.1 | 19,132 |
| 108 | 140.8 | 17,601 | 148.5 | 18,571 | 141.4 | 17,484 | 149.2 | 18,444 | 145.2 | 18,173 | 153.9 | 19,251 | 145.9 | 18,049 | 154.5 | 19,116 |
| 109 | 141.6 | 17,532 | 149.9 | 18,554 | 142.2 | 17,416 | 150.5 | 18,427 | 146.1 | 18,099 | 155.2 | 19,235 | 146.7 | 17,975 | 155.3 | 19,032 |
| 110 | 142.5 | 17,465 | 151.2 | 18,536 | 143.1 | 17,349 | 151.8 | 18,410 | 146.9 | 18,025 | 155.3 | 19,061 | 147.5 | 17,903 | 155.3 | 18,850 |

| Project Head (feet) | Unit 12 w/ Blades Locked at ~27.8 ° (Feb 2016) |  |  |  |  |  |  |  | Unit 14 w/ Blades Locked at ~29.6° (Aug 2019) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | With STS |  |  |  | No STS |  |  |  | With STS |  |  |  | No STS |  |  |  |
|  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  | Lower Limit |  | Upper Limit |  |
|  | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 80 | 99.6 | 17,333 | 105.0 | 18276.0 | 100.0 | 17,210 | 105.5 | 18,142 | 106.5 | 18,639 | 110.6 | 19,356 | 106.9 | 18,501 | 111.0 | 19,210 |
| 81 | 100.9 | 17,313 | 106.2 | 18,226 | 101.4 | 17,190 | 106.7 | 18,093 | 107.9 | 18,617 | 111.9 | 19,304 | 108.3 | 18,479 | 112.3 | 19,158 |
| 82 | 102.2 | 17,293 | 107.5 | 18,177 | 102.7 | 17,171 | 107.9 | 18,045 | 109.3 | 18,596 | 113.2 | 19,252 | 109.7 | 18,458 | 113.6 | 19,107 |
| 83 | 103.5 | 17,272 | 108.7 | 18,129 | 104.0 | 17,151 | 109.1 | 17,997 | 110.7 | 18,573 | 114.4 | 19,200 | 111.2 | 18,436 | 114.9 | 19,056 |
| 84 | 104.9 | 17,252 | 109.9 | 18,081 | 105.3 | 17,131 | 110.4 | 17,950 | 112.1 | 18,551 | 115.7 | 19,149 | 112.6 | 18,415 | 116.2 | 19,006 |
| 85 | 106.2 | 17,231 | 111.1 | 18,033 | 106.6 | 17,110 | 111.6 | 17,904 | 113.5 | 18,528 | 117.0 | 19,099 | 114.0 | 18,393 | 117.5 | 18,956 |
| 86 | 107.8 | 17,265 | 112.6 | 18,038 | 108.3 | 17,145 | 113.1 | 17,909 | 115.2 | 18,565 | 118.6 | 19,104 | 115.7 | 18,430 | 119.0 | 18,961 |
| 87 | 109.4 | 17,298 | 114.2 | 18,061 | 109.9 | 17,178 | 114.7 | 17,932 | 117.0 | 18,601 | 120.3 | 19,132 | 117.4 | 18,465 | 120.8 | 18,990 |
| 88 | 111.0 | 17,330 | 115.8 | 18,083 | 111.5 | 17,209 | 116.3 | 17,954 | 118.7 | 18,634 | 122.0 | 19,159 | 119.2 | 18,499 | 122.5 | 19,017 |
| 89 | 112.6 | 17,360 | 117.4 | 18,104 | 113.1 | 17,240 | 117.9 | 17,975 | 120.4 | 18,667 | 123.7 | 19,185 | 120.9 | 18,531 | 124.2 | 19,043 |
| 90 | 114.2 | 17,389 | 118.6 | 18,051 | 114.7 | 17,269 | 119.1 | 17,922 | 122.1 | 18,698 | 124.9 | 19,116 | 122.6 | 18,562 | 125.4 | 18,975 |
| 91 | 115.6 | 17,388 | 120.2 | 18,079 | 116.1 | 17,268 | 120.7 | 17,950 | 123.6 | 18,697 | 126.6 | 19,146 | 124.1 | 18,561 | 127.1 | 19,005 |
| 92 | 117.0 | 17,386 | 121.9 | 18,106 | 117.5 | 17,267 | 122.4 | 17,977 | 125.1 | 18,695 | 128.3 | 19,174 | 125.6 | 18,560 | 128.8 | 19,033 |
| 93 | 118.4 | 17,384 | 123.5 | 18,132 | 118.9 | 17,265 | 124.0 | 18,003 | 126.6 | 18,692 | 130.0 | 19,202 | 127.1 | 18,558 | 130.6 | 19,060 |
| 94 | 119.8 | 17,382 | 125.1 | 18,156 | 120.3 | 17,263 | 125.7 | 18,028 | 128.1 | 18,690 | 131.8 | 19,228 | 128.6 | 18,555 | 132.3 | 19,087 |
| 95 | 121.2 | 17,379 | 126.8 | 18,180 | 121.7 | 17,260 | 127.3 | 18,052 | 129.6 | 18,687 | 133.5 | 19,253 | 130.1 | 18,553 | 134.0 | 19,112 |
| 96 | 122.6 | 17,393 | 128.3 | 18,193 | 123.2 | 17,274 | 128.8 | 18,065 | 131.1 | 18,701 | 135.1 | 19,267 | 131.7 | 18,567 | 135.6 | 19,126 |
| 97 | 124.1 | 17,406 | 129.8 | 18,206 | 124.6 | 17,287 | 130.3 | 18,078 | 132.7 | 18,715 | 136.7 | 19,280 | 133.2 | 18,581 | 137.2 | 19,139 |
| 98 | 125.6 | 17,418 | 131.3 | 18,218 | 126.1 | 17,299 | 131.9 | 18,090 | 134.2 | 18,728 | 138.3 | 19,292 | 134.8 | 18,594 | 138.8 | 19,151 |
| 99 | 127.0 | 17,430 | 132.8 | 18,229 | 127.6 | 17,311 | 133.4 | 18,101 | 135.8 | 18,741 | 139.9 | 19,304 | 136.3 | 18,607 | 140.4 | 19,164 |
| 100 | 128.5 | 17,441 | 134.3 | 18,240 | 129.0 | 17,323 | 134.9 | 18,112 | 137.3 | 18,753 | 141.5 | 19,316 | 137.9 | 18,619 | 142.0 | 19,175 |
| 101 | 129.7 | 17,419 | 135.8 | 18,240 | 130.2 | 17,301 | 136.3 | 18,112 | 138.6 | 18,729 | 143.0 | 19,315 | 139.2 | 18,596 | 143.5 | 19,175 |
| 102 | 130.9 | 17,397 | 137.2 | 18,239 | 131.4 | 17,279 | 137.8 | 18,111 | 139.9 | 18,706 | 144.5 | 19,314 | 140.5 | 18,572 | 145.1 | 19,174 |
| 103 | 132.1 | 17,376 | 138.6 | 18,238 | 132.7 | 17,258 | 139.2 | 18,110 | 141.2 | 18,682 | 146.0 | 19,313 | 141.8 | 18,549 | 146.6 | 19,173 |
| 104 | 133.3 | 17,354 | 140.1 | 18,237 | 133.9 | 17,237 | 140.6 | 18,109 | 142.5 | 18,659 | 147.5 | 19,312 | 143.1 | 18,526 | 148.1 | 19,172 |
| 105 | 134.5 | 17,333 | 141.5 | 18,235 | 135.1 | 17,216 | 142.1 | 18,108 | 143.8 | 18,636 | 149.0 | 19,310 | 144.4 | 18,504 | 149.6 | 19,170 |
| 106 | 135.3 | 17,263 | 142.8 | 18,218 | 135.9 | 17,146 | 143.4 | 18,091 | 144.7 | 18,561 | 150.3 | 19,277 | 145.3 | 18,429 | 150.7 | 19,122 |
| 107 | 136.1 | 17,194 | 144.1 | 18,201 | 136.7 | 17,078 | 144.7 | 18,074 | 145.6 | 18,487 | 151.5 | 19,244 | 146.2 | 18,356 | 151.9 | 19,074 |
| 108 | 137.0 | 17,127 | 145.4 | 18,184 | 137.6 | 17,011 | 146.0 | 18,057 | 146.4 | 18,414 | 152.8 | 19,211 | 147.0 | 18,284 | 153.0 | 19,027 |
| 109 | 137.8 | 17,060 | 146.7 | 18,167 | 138.4 | 16,945 | 147.3 | 18,040 | 147.3 | 18,343 | 154.0 | 19,179 | 147.9 | 18,213 | 154.2 | 18,980 |
| 110 | 138.6 | 16,994 | 148.0 | 18,150 | 139.2 | 16,880 | 148.7 | 18,024 | 148.2 | 18,272 | 155.3 | 19,147 | 148.8 | 18,143 | 155.3 | 18,934 |

- Units 4, 8, 9, 11, 12, and 14 have runner blades that are locked at a fixed angle (non-adjustable) and a restricted operating range until the unit is repaired.