# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:  	20LMN004 – Units 4 & 5 Locked Blades

Date Submitted:		13 January 2020

Project:			Lower Monumental Dam

Requester Name, Agency:	Lisa Wright, Corps RCC

Final Action:			APPROVED 23-JAN-2020

FPP Section:  Table LMN-6. Turbine Unit Operating Ranges.

Justification for Change:

Need to add the updated operating range for LMN Units 4 and 5 with hydraulically locked blades (see FPOM MFR 20 LMN 01, emailed 01/06/2020). Until the blade seals are replaced, the units are restricted to smaller operating ranges, as follows:

- Unit 4 locked at 25° (upper 1%) = approx. 17.8 – 19.0 kcfs

- Unit 5 locked at 22° (mid 1%) = range TBD pending index test in February 2020.

Proposed Change:

See next page with edits to existing Table LMN-5 in track changes.

Comments:

23-JAN-2020 FPOM FPP Meeting: Unit 5 range is still pending index testing. Wright will add in that range as soon as it’s available.

3-FEB-2020 UPDATE: The project confirmed that Unit 5 index test results won’t be finalized until March 2020, after the FPP is printed. Therefore, the FPP operating range for Unit 5 will be “TBD”. Once the results are available, an updated change form will be coordinated with FPOM.

Record of Final Action:  APPROVED at the FPOM FPP meeting 1/23/2020. Unit 5 range will be added as soon as it’s available.

Table LMN-6. Lower Monumental Dam Turbine Unit Power (MW) and Flow (cfs) at ±1% of Peak Turbine Efficiency (Lower and Upper Limits of 1% Range) and Operating Limits. a

| Project | LMN Units 1, 2b, 3 – with STS |  |  |  |  |  |  | LMN Units 1, 2b, 3 – No STS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit |  | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit |  |
| (feet) | MW | cfs |  | MW | cfs | MW | cfs | MW | cfs |  | MW | cfs | MW | cfs |
| 85 | 68.6 | 11,169 |  | 128.5 | 20,905 | 140.9 | 24,344 | 69.2 | 11,123 |  | 125.8 | 20,216 | 140.9 | 23,569 |
| 86 | 69.4 | 11,154 |  | 131.0 | 21,056 | 142.8 | 24,273 | 70.0 | 11,109 |  | 128.3 | 20,363 | 142.8 | 23,542 |
| 87 | 70.2 | 11,140 |  | 133.5 | 21,204 | 144.6 | 24,200 | 70.8 | 11,094 |  | 130.8 | 20,506 | 144.6 | 23,513 |
| 88 | 70.9 | 11,125 |  | 136.1 | 21,348 | 146.5 | 24,126 | 71.6 | 11,080 |  | 133.3 | 20,645 | 146.5 | 23,482 |
| 89 | 71.7 | 11,111 |  | 138.6 | 21,488 | 148.3 | 24,050 | 72.3 | 11,066 |  | 135.8 | 20,781 | 148.3 | 23,450 |
| 90 | 72.4 | 11,097 |  | 141.2 | 21,625 | 150.2 | 23,974 | 73.1 | 11,052 |  | 138.3 | 20,913 | 150.2 | 23,415 |
| 91 | 73.3 | 11,088 |  | 141.6 | 21,418 | 151.5 | 23,815 | 74.0 | 11,043 |  | 138.7 | 20,714 | 151.5 | 23,268 |
| 92 | 74.1 | 11,079 |  | 142.0 | 21,216 | 152.8 | 23,654 | 74.8 | 11,035 |  | 139.1 | 20,518 | 152.8 | 23,119 |
| 93 | 75.0 | 11,071 |  | 142.4 | 21,018 | 154.0 | 23,492 | 75.7 | 11,026 |  | 139.5 | 20,327 | 154.0 | 22,968 |
| 94 | 75.8 | 11,061 |  | 142.8 | 20,824 | 155.2 | 23,420 | 76.5 | 11,017 |  | 139.9 | 20,140 | 155.2 | 22,850 |
| 95 | 76.7 | 11,052 |  | 143.2 | 20,634 | 155.2 | 22,904 | 77.4 | 11,009 |  | 140.3 | 19,956 | 155.2 | 22,409 |
| 96 | 77.7 | 11,071 |  | 143.3 | 20,416 | 155.2 | 22,592 | 78.4 | 11,027 |  | 140.4 | 19,746 | 155.2 | 22,125 |
| 97 | 78.8 | 11,088 |  | 143.5 | 20,203 | 155.2 | 22,286 | 79.5 | 11,044 |  | 140.6 | 19,540 | 155.2 | 21,847 |
| 98 | 79.8 | 11,105 |  | 143.6 | 19,994 | 155.2 | 21,988 | 80.5 | 11,061 |  | 140.7 | 19,338 | 155.2 | 21,576 |
| 99 | 80.8 | 11,121 |  | 143.8 | 19,789 | 155.2 | 21,696 | 81.5 | 11,078 |  | 140.9 | 19,141 | 155.2 | 21,309 |
| 100 | 81.8 | 11,137 |  | 144.0 | 19,589 | 155.2 | 21,410 | 82.6 | 11,093 |  | 141.0 | 18,947 | 155.2 | 21,049 |
| 101 | 82.7 | 11,138 |  | 145.9 | 19,641 | 155.2 | 21,130 | 83.5 | 11,095 |  | 142.9 | 18,998 | 155.2 | 20,798 |
| 102 | 83.6 | 11,140 |  | 147.8 | 19,692 | 155.2 | 20,857 | 84.3 | 11,096 |  | 144.8 | 19,047 | 155.2 | 20,553 |
| 103 | 84.5 | 11,141 |  | 149.7 | 19,741 | 155.2 | 20,589 | 85.2 | 11,098 |  | 146.7 | 19,095 | 155.2 | 20,312 |
| 104 | 85.4 | 11,142 |  | 151.6 | 19,789 | 155.2 | 20,326 | 86.1 | 11,099 |  | 148.5 | 19,142 | 155.2 | 20,077 |
| 105 | 86.2 | 11,143 |  | 153.5 | 19,837 | 155.2 | 20,069 | 87.0 | 11,100 |  | 150.4 | 19,188 | 155.2 | 19,846 |
|  | LMN Units 4b, 5b, 6 – with STS |  |  |  |  |  |  | LMN Units 4b, 5b, 6 – No STS |  |  |  |  |  |  |
| 85 | 89.8 |  | 14,150 | 123.8 | 19,493 | 141.3 | 25,052 | 89.5 |  | 13,962 | 122.5 | 19,102 | 141.3 | 24,441 |
| 86 | 91.0 |  | 14,160 | 125.5 | 19,519 | 143.3 | 24,978 | 90.7 |  | 13,971 | 124.2 | 19,128 | 143.3 | 24,414 |
| 87 | 92.2 |  | 14,169 | 127.2 | 19,545 | 145.4 | 24,904 | 91.9 |  | 13,981 | 125.9 | 19,153 | 145.4 | 24,385 |
| 88 | 93.4 |  | 14,178 | 128.9 | 19,569 | 147.4 | 24,829 | 93.1 |  | 13,990 | 127.6 | 19,177 | 147.4 | 24,356 |
| 89 | 94.6 |  | 14,187 | 130.6 | 19,593 | 149.4 | 24,753 | 94.2 |  | 13,998 | 129.3 | 19,201 | 149.4 | 24,324 |
| 90 | 95.7 |  | 14,195 | 132.3 | 19,616 | 151.4 | 24,676 | 95.4 |  | 14,006 | 131.0 | 19,224 | 151.4 | 24,291 |
| 91 | 96.9 |  | 14,196 | 133.9 | 19,613 | 153.5 | 24,623 | 96.5 |  | 14,007 | 132.5 | 19,221 | 153.5 | 24,230 |
| 92 | 98.0 |  | 14,197 | 135.4 | 19,610 | 155.2 | 24,553 | 97.7 |  | 14,008 | 134.0 | 19,218 | 155.2 | 24,168 |
| 93 | 99.2 |  | 14,197 | 136.9 | 19,607 | 155.2 | 23,936 | 98.8 |  | 14,009 | 135.5 | 19,215 | 155.2 | 23,577 |
| 94 | 100.3 |  | 14,198 | 138.5 | 19,603 | 155.2 | 23,343 | 99.9 |  | 14,010 | 137.1 | 19,211 | 155.2 | 23,008 |
| 95 | 101.4 |  | 14,198 | 140.0 | 19,600 | 155.2 | 22,771 | 101.1 |  | 14,010 | 138.6 | 19,208 | 155.2 | 22,460 |
| 96 | 102.3 |  | 14,170 | 140.5 | 19,456 | 155.2 | 22,389 | 102.0 |  | 13,982 | 139.1 | 19,067 | 155.2 | 21,828 |
| 97 | 103.2 |  | 14,142 | 141.0 | 19,315 | 155.2 | 22,017 | 102.9 |  | 13,954 | 139.6 | 18,929 | 155.2 | 21,478 |
| 98 | 104.1 |  | 14,114 | 141.5 | 19,177 | 155.2 | 21,654 | 103.8 |  | 13,928 | 140.1 | 18,794 | 155.2 | 21,136 |
| 99 | 105.1 |  | 14,087 | 142.0 | 19,042 | 155.2 | 21,300 | 104.7 |  | 13,901 | 140.5 | 18,662 | 155.2 | 20,803 |
| 100 | 106.0 |  | 14,061 | 142.5 | 18,909 | 155.2 | 20,955 | 105.6 |  | 13,875 | 141.0 | 18,532 | 155.2 | 20,723 |
| 101 | 107.3 |  | 14,091 | 143.9 | 18,909 | 155.2 | 20,701 | 106.9 |  | 13,904 | 142.5 | 18,532 | 155.2 | 20,477 |
| 102 | 108.5 |  | 14,120 | 145.4 | 18,909 | 155.2 | 20,452 | 108.2 |  | 13,933 | 143.9 | 18,532 | 155.2 | 20,236 |
| 103 | 109.8 |  | 14,149 | 146.8 | 18,909 | 155.2 | 20,208 | 109.4 |  | 13,962 | 145.3 | 18,532 | 155.2 | 19,999 |
| 104 | 111.1 |  | 14,177 | 148.2 | 18,909 | 155.2 | 19,970 | 110.7 |  | 13,989 | 146.7 | 18,532 | 155.2 | 19,768 |
| 105 | 112.4 |  | 14,204 | 149.6 | 18,909 | 155.2 | 19,736 | 112.0 |  | 14,017 | 148.1 | 18,532 | 155.2 | 19,541 |

- Values provided by HDC (July 2003). Flow (cfs) was calculated based on turbine efficiency, project head, and power output (MW). “Operating Limit” is the maximum safe operating point based on cavitation or generator limit (added Feb 2018).

- Units 2, 4, and 5 have hydraulically locked runner blades due to leaking blade seals. Until the blade seals are replaced, the units are restricted to smaller operating ranges of: Unit 2 = 15-17 kcfs; Unit 4 = 17-19 kcfs; Unit 5 = TBD.