# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:  	20LMN005 – Operating Range Tables for Locked-Blade Units

Date Submitted:		5 February 2020; Updated 16 March 2020

Project:			Lower Monumental Dam

Requester Name, Agency:	Lisa Wright, Corps RCC

Final Action:			APPROVED 13-FEB-2020

FPP Section:

Table LMN-6. Turbine Unit Operating Ranges.

Justification for Change:

Need to add a table of operating ranges for LMN Units 2, 4 and 5 with locked runner blades. Until now, the ranges have been estimated in a footnote to the table. Adding a table for each unit defines the operating limits over a range of heads.

UPDATE 16-MAR-2020: Unit 5 range has been added to the table with Unit 4. An abbreviated index test was conducted on Unit 5 on 12-FEB-2020 and the recommendation was to use the same operating tables as Unit 4 as long as the blades for both units remain locked at 25°.

Proposed Change:

See next page with edits to existing Table LMN-6 in track changes.

Updates made on 16-MAR-2020 highlighted in yellow.

Comments:

Record of Final Action: Approved at the FPOM meeting on 13-FEB-2020.

Table LMN-6-A. Temporary Operating Range Values for Lower Monumental Units 2, 4, and 5 with Locked Runner Blades (Non-Adjustable). a

| Project | LMN Unit 2 (Blades Locked at 25°) – with STS |  |  |  |  |  | LMN Units 4 and 5 (Blades Locked at 25°) – with STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | Lower Limit |  | Peak Efficiency |  | Upper Limit |  | Lower Limit |  | Peak Efficiency |  | Upper Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 85 | 91.6 | 15,202 | 95.8 | 15,804 | 98.6 | 16,361 | 111.2 | 17,959 | 113.5 | 18,226 | 116.3 | 18,791 |
| 86 | 93.0 | 15,233 | 97.1 | 15,805 | 100.0 | 16,380 | 112.5 | 17,951 | 114.9 | 18,223 | 117.8 | 18,794 |
| 87 | 94.4 | 15,262 | 98.3 | 15,806 | 101.4 | 16,398 | 113.9 | 17,942 | 116.3 | 18,220 | 119.3 | 18,796 |
| 88 | 95.8 | 15,290 | 99.6 | 15,807 | 102.8 | 16,415 | 115.2 | 17,933 | 117.7 | 18,216 | 120.8 | 18,798 |
| 89 | 97.2 | 15,317 | 100.9 | 15,807 | 104.3 | 16,432 | 116.6 | 17,924 | 119. 1 | 18,212 | 122.3 | 18,800 |
| 90 | 98.6 | 15,343 | 102.1 | 15,807 | 105.7 | 16,447 | 117.9 | 17,915 | 120.6 | 18,207 | 123.8 | 18,801 |
| 91 | 99.8 | 15,342 | 103.4 | 15,809 | 107.0 | 16,449 | 119.6 | 17,954 | 122.2 | 18,233 | 125.3 | 18,810 |
| 92 | 101.0 | 15,340 | 104.7 | 15,811 | 108.3 | 16,451 | 121.3 | 17,991 | 123.8 | 18,257 | 126.8 | 18,818 |
| 93 | 102.2 | 15,339 | 106.0 | 15,813 | 109.6 | 16,452 | 122.9 | 18,028 | 125.4 | 18,280 | 128.4 | 18,826 |
| 94 | 103.4 | 15,337 | 107.2 | 15,814 | 110.9 | 16,453 | 124.6 | 18,063 | 127.0 | 18,303 | 129.9 | 18,833 |
| 95 | 104.6 | 15,334 | 108.5 | 15,815 | 112.2 | 16,453 | 126.3 | 18,097 | 128.6 | 18,325 | 131.4 | 18,840 |
| 96 | 105.9 | 15,352 | 109.5 | 15,784 | 113.6 | 16,466 | 127.6 | 18,091 | 130.0 | 18,327 | 133.0 | 18,852 |
| 97 | 107.2 | 15,368 | 110.5 | 15,753 | 114.9 | 16,478 | 128.9 | 18,086 | 131.4 | 18,329 | 134.5 | 18,863 |
| 98 | 108.5 | 15,384 | 111.5 | 15,723 | 116.3 | 16,489 | 130.3 | 18,080 | 132.8 | 18,330 | 136.0 | 18,873 |
| 99 | 109.8 | 15,400 | 112.5 | 15,693 | 117.6 | 16,500 | 131.6 | 18,074 | 134.3 | 18,332 | 137.5 | 18,883 |
| 100 | 111.1 | 15,415 | 113.5 | 15,663 | 119.0 | 16,510 | 133.0 | 18,069 | 135.7 | 18,333 | 139.1 | 18,893 |
| 101 | 112.2 | 15,403 | 114.9 | 15,692 | 120.4 | 16,530 | 134.3 | 18,059 | 137. 1 | 18,339 | 140.6 | 18,918 |
| 102 | 113.3 | 15,391 | 116.4 | 15,719 | 121.8 | 16,549 | 135.5 | 18,050 | 138.5 | 18,345 | 142.2 | 18,943 |
| 103 | 114.4 | 15,380 | 117.8 | 15,746 | 123.3 | 16,568 | 136.8 | 18,041 | 140.0 | 18,351 | 143.8 | 18,967 |
| 104 | 115.5 | 15,368 | 119.2 | 15,772 | 124.7 | 16,586 | 138.1 | 18,032 | 141.4 | 18,357 | 145.4 | 18,991 |
| 105 | 116.6 | 15,356 | 120.7 | 15,797 | 126.1 | 16,603 | 139.4 | 18,024 | 142.8 | 18,362 | 147.0 | 19,014 |

- Units 2, 4, and 5 have hydraulically locked (non-adjustable) runner blades due to leaking blade seals and are restricted to a smaller operating range until the blade seals are repaired or replaced. Values provided by HDC based on the abbreviated index test for Unit 2 (Feb 2019), Unit 4 (Jan 2018), and Unit 5 (Feb 2020).