# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:  	20MCN002 – Automated Temperature Monitoring

Date Submitted:		16 December 2019

Project:			McNary Dam

Requester Name, Agency:	Ann Setter, COE NWW

Final Action:			WITHDRAWN 1/29/2020

FPP Section:  MCN section 2.4.2.13 – Adult Facilities / Fish Passage Season

Justification for Change:  The Corps now has automated temperature monitoring at all 5 NWW facilities. The FPP criteria for installing fishway temperature monitors are now obsolete.

Proposed Change: [see below for edits to existing FPP in track changes]

2.4.2.13. Fishway Temperature Monitoring. From June 1 through September 30, water temperature will be monitored at adult fishway entrances and exits.

            - Temperature monitors shall be within 10 meters of all shore-oriented entrances and exits.

            - If possible, the entrance monitor shall be within 1 meter above the ladder floor and at least 10 meters downstream of ladder diffusers to allow for sufficient mixing with surface water.

            - The exit monitor shall be within 1 meter above the ladder floor and above all diffusers to allow for sufficient mixing with surface water.

            - If an existing temperature monitoring location is proposed to be used for either the exit or entrance, it shall be verified that the site accurately reflects water temperature within 10 meters of the entrance or exit.

            - The Fish Passage Center (FPC) will post the data online on a weekly basis at: www.fpc.org/river/Q_ladderwatertempgraph.php

Comments: 	Listed oldest to newest.

1/23/2020 FPOM FPP Meeting: The original proposal was to delete sub-sections i–iv since the temperature monitors are permanent and automated. Lorz asked that the criteria be left in to ensure the locations are accurate.

1/24/2020 email from Ann Setter to FPOM: “The real time water temperature data collection probes located within the Walla Walla district fish ladders are calibrated annually. They are within 0.1-0.2% accuracy. Data update hourly with a 2-3 hr processing delay. Data collection occurs throughout the year and is not limited to the June-Sept period which was applicable when hobos were being installed annually.”

1/24/2020 email from Chris Peery to FPOM: “Just a minor clarification. The temperature sensors being used in the fishways are typically accurate to within +- 0.1 degrees C and they are checked annually for accuracy to assure they are operating within specifications.”

1/24/2020 email from Erick Van Dyke to FPOM: “I feel it would be my preference that the FPP stress that ladder temperature data for all dates that it is available are shared via the pseudo real-time web links that have been used to date (e.g., FPC). FPOM, would this provide a reasonable expectation of dissemination and access to ladder temperature data (fish passage information) given no one is asking that periods when no information is available be made available? I would be ok with this kind of caveat in the FPP change language for each project.”

1/29/2020 email from Ann Setter to FPOM: “We have decided based on comments at FPP meeting and your [Erick’s] comments to withdraw the change forms and maintain the current FPP language for 2020.  My understanding is that FPC currently downloads water temp data April - Aug from the Corps for posting in case you are not already aware.  Thanks for the input.”

1/29/2020 email from Charles Morrill to FPOM: “I concur that keeping the current language works.”

Record of Final Action:  WITHDRAWN 1/29/2020