# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:  	20MCN003 – Operating Range Table for Locked-Blade Unit 6

Date Submitted:		5 February 2020

Project:			McNary Dam

Requester Name, Agency:	Lisa Wright, Corps RCC

Final Action:			APPROVED 13-FEB-2020

FPP Section:

Table MCN-6. Turbine Unit Operating Ranges.

Justification for Change:

Need to add a table for Unit 6 operating range with locked runner blades. Until now, the range has been estimated in a footnote to the table. Adding a separate table defines the operating limits over a range of heads.

Proposed Change:

See next page with edits to existing Table MCN-6 in track changes.

Comments:

Record of Final Action:  Approved at the FPOM meeting on 13-FEB-2020.

Table MCN-6-A. Temporary Operating Range Values for McNary Unit 6 with Locked Runner Blades (Non-Adjustable). a

| Project | MCN Unit 6 (Blades Locked at 22°) – With ESBS |  |  |  |  |  | MCN Unit 6 (Blades Locked at 22°) – No ESBS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | Lower Limit |  | Peak Efficiency |  | Upper Limit |  | Lower Limit |  | Peak Efficiency |  | Upper Limit |  |
| (feet) | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 62 | 46.8 | 10,665 | 49.1 | 11,130 | 49.8 | 11,345 | 47.6 | 10,648 | 49.9 | 11,078 | 50.5 | 11,289 |
| 63 | 47.5 | 10,659 | 50.1 | 11,175 | 50.9 | 11,405 | 48.4 | 10,641 | 50.9 | 11,122 | 51.6 | 11,348 |
| 64 | 48.3 | 10,652 | 51.2 | 11,218 | 52.0 | 11,462 | 49.2 | 10,635 | 52.0 | 11,165 | 52.8 | 11,405 |
| 65 | 49.1 | 10,645 | 52.2 | 11,259 | 53.1 | 11,517 | 50.0 | 10,628 | 53.0 | 11,205 | 53.9 | 11,460 |
| 66 | 49.9 | 10,647 | 53.1 | 11,255 | 54.0 | 11,511 | 50.9 | 10,631 | 53.9 | 11,202 | 54.8 | 11,455 |
| 67 | 50.8 | 10,649 | 54.0 | 11,251 | 54.9 | 11,505 | 51.7 | 10,633 | 54.8 | 11,198 | 55.7 | 11,449 |
| 68 | 51.7 | 10,650 | 54.9 | 11,246 | 55.8 | 11,498 | 52.6 | 10,634 | 55.7 | 11,194 | 56.6 | 11,443 |
| 69 | 52.5 | 10,650 | 55.8 | 11,241 | 56.7 | 11,491 | 53.5 | 10,635 | 56.6 | 11,189 | 57.5 | 11,436 |
| 70 | 53.4 | 10,650 | 56.6 | 11,235 | 57.6 | 11,484 | 54.4 | 10,635 | 57.5 | 11,184 | 58.4 | 11,429 |
| 71 | 54.5 | 10,697 | 57.6 | 11,256 | 58.5 | 11,497 | 55.5 | 10,682 | 58.5 | 11,205 | 59.4 | 11,443 |
| 72 | 55.6 | 10,742 | 58.7 | 11,275 | 59.5 | 11,509 | 56.6 | 10,728 | 59.6 | 11,225 | 60.4 | 11,455 |
| 73 | 56.6 | 10,785 | 59.7 | 11,294 | 60.5 | 11,521 | 57.7 | 10,771 | 60.6 | 11,244 | 61.4 | 11,467 |
| 74 | 57.7 | 10,827 | 60.7 | 11,311 | 61.5 | 11,531 | 58.8 | 10,813 | 61.6 | 11,262 | 62.4 | 11,478 |
| 75 | 58.8 | 10,866 | 61.7 | 11,328 | 62.5 | 11,541 | 59.9 | 10,853 | 62.6 | 11,279 | 63.4 | 11,488 |
| 76 | 59.8 | 10,888 | 62.8 | 11,368 | 63.6 | 11,587 | 60.9 | 10,875 | 63.7 | 11,319 | 64.6 | 11,534 |
| 77 | 60.7 | 10,909 | 63.8 | 11,407 | 64.7 | 11,631 | 61.8 | 10,896 | 64.8 | 11,357 | 65.7 | 11,578 |
| 78 | 61.6 | 10,929 | 64.9 | 11,444 | 65.8 | 11,674 | 62.8 | 10,916 | 65.9 | 11,395 | 66.8 | 11,620 |
| 79 | 62.6 | 10,949 | 66.0 | 11,481 | 66.9 | 11,715 | 63.7 | 10,936 | 67.0 | 11,431 | 67.9 | 11,662 |
| 80 | 63.5 | 10,968 | 67.0 | 11,516 | 68.0 | 11,755 | 64.7 | 10,955 | 68.1 | 11,466 | 69.1 | 11,702 |
| 81 | 64.4 | 10,991 | 68.0 | 11,529 | 69.0 | 11,765 | 65.6 | 10,978 | 69.0 | 11,479 | 70.0 | 11,712 |
| 82 | 65.4 | 11,013 | 68.9 | 11,541 | 69.9 | 11,775 | 66.6 | 11,000 | 70.0 | 11,492 | 71.0 | 11,721 |
| 83 | 66.3 | 11,035 | 69.8 | 11,553 | 70.8 | 11,784 | 67.5 | 11,022 | 70.9 | 11,504 | 71.9 | 11,731 |
| 84 | 67.3 | 11,056 | 70.8 | 11,565 | 71.7 | 11,793 | 68.5 | 11,043 | 71.8 | 11,515 | 72.8 | 11,740 |
| 85 | 68.2 | 11,076 | 71.7 | 11,576 | 72.7 | 11,802 | 69.5 | 11,063 | 72.8 | 11,527 | 73.8 | 11,749 |
| 86 | 69.2 | 11,117 | 72.6 | 11,590 | 73.5 | 11,808 | 70.5 | 11,104 | 73.7 | 11,541 | 74.7 | 11,755 |
| 87 | 70.3 | 11,158 | 73.5 | 11,604 | 74.4 | 11,815 | 71.6 | 11,145 | 74.7 | 11,555 | 75.6 | 11,761 |

- Unit 6 has hydraulically locked runner blades to prevent oil leaks and is restricted to a smaller operating range until the unit is repaired. Values provided by HDC based on the abbreviated index test in Jan 2019.