# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:  	21JDA002 – Updates for Locked-Blade Units

Date Submitted:		31 December 2020

Project:			John Day Dam

Requester Name, Agency:	Lisa Wright, Corps RCC

Final Action:			APPROVED – 28 January 2021

FPP Section:

Table JDA-7-A. Turbine Operating Ranges for Units with Locked Runner Blades.

Justification for Change:

Update the table of turbine operating ranges for units with locked runner blades:

- Add Units 3 and 10. The operating ranges provided are preliminary until index test results are finalized. The FPP will be updated when the final ranges are available.

- Remove Unit 12. The unit is being rehabbed to adjustable-blade.

Proposed Change:

See next page with edits to existing Table JDA-7-A in track changes.

Comments:

28-JAN-2021 FPOM FPP Meeting:

- Wright noted that the Unit 3 index test results were just finalized this week so she will update the table with the final Unit 3 operating range. Unit 10 will be updated as soon as the range is finalized.

- Lorz requested adding whether the unit is hydraulically locked or welded. Wright will add that information into the table.

Record of Final Action:

Approved as revised with the final Unit 3 range and added info on how the blades are locked (hydraulically or welded).

Table JDA-7-A. Operating Range Values for John Day Turbine Units 3, 4, 8, 9, 10, 11, and 14 with Locked Runner Blades

(Non-Adjustable). a

- Units 3, 4, 8, 9, 10, 11, and 14 have runner blades that are locked at a fixed angle (non-adjustable) and a restricted operating range until the unit is repaired.