# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	21MCN002 – McNary Dam modified spill tables

Date Submitted:		18 December 2020

Project:  			McNary Dam

Requester Name, Agency:	William Gersbach. CENWW-ODM

Final Action:			APPROVED – 11 February 2021

FPP Section:  Spill Pattern Tables MCN-7 (with TSWs) and MCN-9 (No TSWs).

Justification for Change: Excessive wear and tear from operating beyond the designed capabilities has increased risk of failure for critical flood emergency response equipment.  Limiting the number of times the electrical relays for spillway cranes are operated will help ensure that they will be fully functional when needed for emergency flood situations.

Proposed Change:  Set the spill gates in bays 2 and 19, at the locations of spillway cranes 6 and 7, to a static opening of gate step 4.

See modified spill pattern tables on the pages below.

Comments:

28-Jan-2021 FPOM FPP Meeting:

- Bettin asked if the TSW patterns could keep bay 2 closed until a higher spill rate, similar to what’s proposed for the no TSW patterns.

- Lorz has concerns with locking bay 2 at four stops for all spill levels and would prefer to see the patterns defined in bands where bay 2 is open a set number of stops over a range of spill (i.e., the project would adjust bay 2 a couple times a season rather than just locking it at four stops). His concern is at higher spill levels there will be a hole in the pattern at bay 2.

- Peery said there are plans to get a new gear box for crane 7 sometime this year but no date yet. So these modified patterns would just be until the fix is made.

- Peery will work with the project and Laughery to see if the patterns can be revised as recommended. PENDING – will be revised and reviewed at FPOM on February 11.

4-FEB-2021 email from Chris Peery: “Attached are revised spill tables for McNary Dam, produced by Ryan Laughery and reviewed by the project, for inclusion with 21MCN002.”

11-FEB-2021 FPOM: Lorz had concerns with certain flow bands where they might have to switch back and forth. Peery responded that issue was considered in the revised patterns. Peery will provide more info on the timeline for repairs. Once they’re complete, the FPP will be changed back to the normal spill patterns.

Record of Final Action:  Approved at the FPOM meeting on 11-FEB-2021.

Table MCN-7. [pg 1 of 5] McNary Dam Spill Patterns for Fish Passage with TSWs in Bays 19-20 and Bay 2 Locked at 4 or 6 Stops.

| MCN Spill Patterns with TSWs (# Gate Stops per Spillbay) and Bay 2 Locked at 4 or 6 Stops (in effect until crane repairs are completed) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total Stops |  | Spill a |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 b | 2 | 3 |  | 4 | 5 | 6 | 7 |  | 8 | 9 |  | 10 |  | 11 | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 | 20 | 21 | 22 b | (#) |  | (kcfs) |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TSW |  | TSW | 1 |  |  | 1 | 21.2 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  | TSW |  | TSW | 1 |  |  | 2 | 23.2 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  | TSW |  | TSW | 1 | 1 |  | 3 | 25.2 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  | TSW |  | TSW | 2 | 1 |  | 4 | 27.1 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 |  | TSW |  | TSW | 2 | 1 |  | 5 | 29.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  | 2 |  | TSW |  | TSW | 2 | 1 |  | 6 | 31.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 1 |  | 7 | 32.9 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 1 |  | 8 | 34.9 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 9 | 36.8 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 |  |  |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 10 | 38.7 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 11 | 40.7 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 12 | 42.6 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 13 | 44.6 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 14 | 46.5 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  |  | 2 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 15 | 48.5 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 2 |  |  | 2 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 16 | 50.4 |
|  |  |  |  |  |  |  |  |  |  | 1 |  |  | 2 |  |  | 2 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 17 | 52.4 |
|  |  |  |  |  |  |  |  |  |  | 2 |  |  | 2 |  |  | 2 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 18 | 54.3 |
|  |  |  |  |  |  |  |  |  |  | 2 | 1 |  | 2 |  |  | 2 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 19 | 56.3 |
|  |  |  |  |  |  |  |  |  |  | 2 | 2 |  | 2 |  |  | 2 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 20 | 58.2 |
|  |  |  |  |  |  |  |  |  |  | 2 | 2 |  | 2 |  |  | 2 |  | 1 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 21 | 60.2 |
|  |  |  |  |  |  |  |  |  |  | 2 | 2 |  | 2 |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 22 | 62.1 |
|  |  |  |  |  |  |  |  |  |  | 2 | 2 |  | 2 |  | 1 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 23 | 64.1 |
|  |  |  |  |  |  |  |  |  |  | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 24 | 66.0 |
|  |  |  |  |  |  |  |  | 1 |  | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 25 | 68.0 |
|  |  |  |  |  |  |  |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 26 | 69.9 |
|  |  |  |  |  | 1 |  |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 27 | 71.9 |
| 2.5 |  | 3.5 |  |  | 2 |  |  | 2 |  | 2 |  |  | 2 |  |  | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 28 | 71.7 |
| 2.5 |  | 3.5 |  |  | 2 | 1 |  | 2 |  | 2 |  |  | 2 |  |  | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 29 | 73.7 |
| 2.5 |  | 3.5 |  |  | 2 | 1 |  | 2 |  | 2 | 1 |  | 2 |  |  | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 30 | 75.7 |
| 2.5 |  | 3.5 |  |  | 2 | 1 |  | 2 |  | 2 | 1 |  | 2 |  | 1 | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 31 | 77.7 |
| 2.5 | 4 | 3.5 |  |  | 2 |  |  | 2 |  | 2 |  |  | 2 |  |  | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 32 | 78.9 |
| 2.5 | 4 | 3.5 |  |  | 2 | 1 |  | 2 |  | 2 |  |  | 2 |  |  | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 33 | 80.9 |
| 2.5 | 4 | 3.5 |  |  | 2 | 1 |  | 2 |  | 2 | 1 |  | 2 |  |  | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 34 | 82.9 |
| 2.5 | 4 | 3.5 |  |  | 2 | 1 |  | 2 |  | 2 | 1 |  | 2 |  | 1 | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 35 | 84.9 |
| 2.5 | 4 | 3.5 |  |  | 2 | 1 |  | 2 | 1 | 2 | 1 |  | 2 |  | 1 | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 36 | 86.9 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 1 |  | 2 | 1 | 2 | 1 |  | 2 |  | 1 | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 2 | 2 |  | 37 | 88.9 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 1 |  | 2 | 1 | 2 | 1 |  | 2 |  | 1 | 2 |  | 1 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 2 |  | 38 | 90.6 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 1 |  | 2 | 1 | 2 | 1 |  | 2 |  | 1 | 2 |  | 2 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 2 |  | 39 | 92.5 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 1 |  | 2 | 1 | 2 | 1 |  | 2 |  | 1 | 2 |  | 2 |  | 2 |  | 1 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 40 | 94.2 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 1 |  | 2 | 1 | 2 | 1 |  | 2 |  | 1 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 41 | 96.1 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 2 |  | 2 | 1 | 2 | 1 |  | 2 |  | 1 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 42 | 98.0 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 2 |  | 2 | 1 | 2 | 2 |  | 2 |  | 1 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 43 | 99.9 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 2 |  | 2 | 1 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 44 | 101.8 |
| 2.5 | 4 | 3.5 | 1 |  | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 45 | 103.7 |
| 2.5 | 4 | 3.5 | 2 |  | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 46 | 105.6 |
| 3 | 4 | 4 | 2 |  | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 47 | 108.9 |
| 3 | 4 | 4 | 2 |  | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 3 |  | 2 |  | 2 |  | TSW |  | TSW | 3 | 3 |  | 48 | 110.6 |
| 3 | 4 | 4 | 2 |  | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 3 |  | 2 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 49 | 112.3 |
| 3 | 4 | 4 | 3 |  | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 3 |  | 2 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 50 | 114.0 |
| 3 | 4 | 4 | 3 |  | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 51 | 115.7 |
| 3 | 4 | 4 | 3 |  | 2 | 3 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 52 | 117.4 |
| 3 | 4 | 4 | 3 |  | 2 | 3 |  | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 53 | 119.1 |
| 3 | 4 | 4 | 3 |  | 2 | 3 |  | 2 | 3 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 54 | 120.8 |
| 3 | 4 | 4 | 3 |  | 2 | 3 |  | 2 | 3 | 2 | 2 |  | 2 |  | 2 | 3 |  | 2 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 55 | 122.5 |
| 3 | 4 | 4 | 3 |  | 2 | 3 |  | 2 | 3 | 2 | 3 |  | 2 |  | 2 | 3 |  | 2 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 56 | 124.2 |
| 3 | 4 | 4 | 3 |  | 2 | 3 |  | 2 | 3 | 2 | 3 |  | 2 |  | 3 | 3 |  | 2 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 57 | 125.9 |
| 3 | 4 | 4 | 3 |  | 2 | 3 |  | 2 | 3 | 2 | 3 |  | 2 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 58 | 127.6 |
| 3 | 4 | 5 | 3 |  | 2 | 3 |  | 2 | 3 | 2 | 3 |  | 2 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 59 | 129.2 |
| 3 | 4 | 5 | 3 |  | 3 | 3 |  | 2 | 3 | 2 | 3 |  | 2 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 60 | 130.9 |
| 3 | 4 | 5 | 3 |  | 3 | 3 |  | 3 | 3 | 2 | 3 |  | 2 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 61 | 132.6 |
| 3 | 4 | 5 | 3 |  | 3 | 3 |  | 3 | 3 | 2 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 62 | 134.3 |
| 3 | 4 | 5 | 3 |  | 3 | 3 |  | 3 | 3 | 2 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 62 | 134.3 |
| 3 | 4 | 5 | 3 |  | 3 | 3 |  | 3 | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 63 | 136.0 |
| 4 | 4 | 5 | 3 |  | 3 | 3 |  | 3 | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | TSW |  | TSW | 3 | 3 |  | 64 | 137.6 |
| 4 | 4 | 5 | 3 |  | 3 | 3 |  | 3 | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 65 | 139.2 |
| 4 | 4 | 5 | 3 |  | 3 | 3 |  | 3 | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 66 | 140.8 |
| 4 | 4 | 5 | 3 |  | 3 | 3 |  | 4 | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 67 | 142.4 |
| 4 | 4 | 5 | 3 |  | 3 | 3 |  | 4 | 3 | 3 | 3 |  | 4 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 68 | 144.0 |
| 4 | 4 | 5 | 3 |  | 4 | 3 |  | 4 | 3 | 3 | 3 |  | 4 |  | 3 | 3 |  | 3 |  | 3 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 69 | 145.6 |
| 4 | 4 | 5 | 3 |  | 4 | 3 |  | 4 | 3 | 3 | 3 |  | 4 |  | 3 | 3 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 70 | 147.2 |
| 4 | 4 | 5 | 3 |  | 4 | 3 |  | 4 | 3 | 4 | 3 |  | 4 |  | 3 | 3 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 71 | 148.8 |
| 4 | 4 | 5 | 3 |  | 4 | 3 |  | 4 | 3 | 4 | 3 |  | 4 |  | 3 | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 72 | 150.4 |
| 4 | 4 | 5 | 3 |  | 4 | 4 |  | 4 | 3 | 4 | 3 |  | 4 |  | 3 | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 73 | 152.0 |
| 4 | 4 | 5 | 3 |  | 4 | 4 |  | 4 | 3 | 4 | 4 |  | 4 |  | 3 | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 74 | 153.6 |
| 4 | 4 | 5 | 3 |  | 4 | 4 |  | 4 | 3 | 4 | 4 |  | 4 |  | 4 | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 75 | 155.2 |
| 4 | 4 | 5 | 3 |  | 4 | 4 |  | 4 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 76 | 156.8 |
| 4 | 4 | 5 | 3 |  | 4 | 4 |  | 4 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 3 |  | 4 |  | 4 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 77 | 158.4 |
| 4 | 4 | 5 | 4 |  | 4 | 4 |  | 4 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 3 |  | 4 |  | 4 |  | 4 |  | 4 |  | TSW |  | TSW | 3 | 3 |  | 78 | 160.0 |
| 4 | 4 | 5 | 4 |  | 4 | 4 |  | 4 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 3 |  | 4 |  | 4 |  | 4 |  | 4 |  | TSW |  | TSW | 4 | 3 |  | 79 | 161.6 |
| 4 | 4 | 5 | 4 |  | 4 | 4 |  | 4 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | TSW |  | TSW | 4 | 3 |  | 80 | 163.2 |
| 5 | 4 | 5 | 4 |  | 4 | 4 |  | 4 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | TSW |  | TSW | 4 | 3 |  | 81 | 164.8 |
| 5 | 4 | 5 | 4 |  | 4 | 4 |  | 4 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 5 |  | TSW |  | TSW | 4 | 3 |  | 82 | 166.4 |
| 5 | 4 | 5 | 4 |  | 4 | 4 |  | 4 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 4 | 3 |  | 83 | 168.0 |
| 5 | 4 | 5 | 4 |  | 4 | 4 |  | 5 | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 4 | 3 |  | 84 | 169.6 |
| 5 | 4 | 5 | 4 |  | 4 | 4 |  | 5 | 4 | 4 | 4 |  | 5 |  | 4 | 4 |  | 4 |  | 4 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 4 | 3 |  | 85 | 171.2 |
| 5 | 4 | 5 | 4 |  | 5 | 4 |  | 5 | 4 | 4 | 4 |  | 5 |  | 4 | 4 |  | 4 |  | 4 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 4 | 3 |  | 86 | 172.8 |
| 5 | 4 | 5 | 4 |  | 5 | 4 |  | 5 | 4 | 4 | 4 |  | 5 |  | 4 | 4 |  | 4 |  | 5 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 4 | 3 |  | 87 | 174.4 |
| 5 | 4 | 5 | 4 |  | 5 | 4 |  | 5 | 4 | 5 | 4 |  | 5 |  | 4 | 4 |  | 4 |  | 5 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 4 | 3 |  | 88 | 176.0 |
| 5 | 4 | 5 | 4 |  | 5 | 4 |  | 5 | 4 | 5 | 4 |  | 5 |  | 4 | 5 |  | 4 |  | 5 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 4 | 3 |  | 89 | 177.6 |
| 5 | 4 | 5 | 4 |  | 5 | 4 |  | 5 | 4 | 5 | 4 |  | 5 |  | 4 | 5 |  | 4 |  | 5 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 3 |  | 90 | 179.2 |
| 5 | 4 | 5 | 4 |  | 5 | 5 |  | 5 | 4 | 5 | 4 |  | 5 |  | 4 | 5 |  | 4 |  | 5 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 3 |  | 91 | 180.8 |
| 5 | 4 | 5 | 4 |  | 5 | 5 |  | 5 | 4 | 5 | 5 |  | 5 |  | 4 | 5 |  | 4 |  | 5 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 3 |  | 92 | 182.4 |
| 5 | 4 | 5 | 4 |  | 5 | 5 |  | 5 | 4 | 5 | 5 |  | 5 |  | 5 | 5 |  | 4 |  | 5 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 3 |  | 93 | 184.0 |
| 5 | 4 | 5 | 4 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 4 |  | 5 |  | 4 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 3 |  | 94 | 185.6 |
| 5 | 4 | 5 | 4 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 4 |  | 5 |  | 5 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 3 |  | 95 | 187.2 |
| 5 | 4 | 5 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 4 |  | 5 |  | 5 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 3 |  | 96 | 188.8 |
| 5 | 4 | 5 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 4 |  | 5 |  | 5 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 4 |  | 97 | 190.4 |
| 5 | 4 | 5 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 4 |  | 98 | 192.0 |
| 5 | 6 | 5 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 4 |  | 5 |  | 5 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 4 |  | 99 | 193.6 |
| 5 | 6 | 5 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | TSW |  | TSW | 5 | 4 |  | 100 | 195.2 |
| 5 | 6 | 5 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 6 |  | TSW |  | TSW | 5 | 4 |  | 101 | 196.8 |
| 5 | 6 | 5 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 6 |  | TSW |  | TSW | 5 | 5 |  | 102 | 198.4 |
| 5 | 6 | 5 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 103 | 200.0 |
| 5 | 6 | 6 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 104 | 201.6 |
| 5 | 6 | 6 | 5 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 5 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 105 | 203.2 |
| 5 | 6 | 6 | 6 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 5 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 106 | 204.8 |
| 5 | 6 | 6 | 6 |  | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 107 | 206.4 |
| 5 | 6 | 6 | 6 |  | 6 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 108 | 208.0 |
| 5 | 6 | 6 | 6 |  | 6 | 5 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 109 | 209.6 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 110 | 211.2 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 5 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 111 | 212.8 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 112 | 214.4 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 5 | 5 | 5 |  | 5 |  | 5 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 113 | 216.0 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 6 | 5 | 5 |  | 5 |  | 5 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 114 | 217.6 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 6 | 5 | 5 |  | 5 |  | 6 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 115 | 219.2 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 6 | 6 | 5 |  | 5 |  | 6 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 116 | 220.8 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 6 | 6 | 5 |  | 6 |  | 6 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 117 | 222.4 |
| 5 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 118 | 224.0 |
| 6 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | TSW |  | TSW | 6 | 5 |  | 119 | 225.6 |
| 6 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 7 |  | TSW |  | TSW | 6 | 5 |  | 120 | 227.2 |
| 6 | 6 | 6 | 6 |  | 6 | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 |  | 6 |  | 6 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 122 | 230.4 |
| 6 | 6 | 7 | 6 |  | 6 | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 |  | 6 |  | 7 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 124 | 233.6 |
| 6 | 6 | 7 | 7 |  | 6 | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 |  | 7 |  | 7 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 126 | 236.8 |
| 6 | 6 | 7 | 7 |  | 7 | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 7 |  | 7 |  | 7 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 128 | 240.0 |
| 6 | 6 | 7 | 7 |  | 7 | 7 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 130 | 243.2 |
| 6 | 6 | 7 | 7 |  | 7 | 7 |  | 7 | 6 | 6 | 6 |  | 6 |  | 6 | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 132 | 246.4 |
| 6 | 6 | 7 | 7 |  | 7 | 7 |  | 7 | 7 | 6 | 6 |  | 6 |  | 7 | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 134 | 249.6 |
| 6 | 6 | 7 | 7 |  | 7 | 7 |  | 7 | 7 | 7 | 6 |  | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 136 | 252.8 |
| 7 | 6 | 7 | 7 |  | 7 | 7 |  | 7 | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | TSW |  | TSW | 7 | 6 |  | 138 | 256.0 |
| 7 | 6 | 7 | 7 |  | 7 | 7 |  | 7 | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | 8 |  | TSW |  | TSW | 7 | 7 |  | 140 | 259.3 |
| 7 | 6 | 8 | 7 |  | 7 | 7 |  | 7 | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 7 |  | 7 |  | 8 |  | TSW |  | TSW | 8 | 7 |  | 142 | 262.7 |
| 7 | 6 | 8 | 8 |  | 7 | 7 |  | 7 | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 7 |  | 8 |  | 8 |  | TSW |  | TSW | 8 | 7 |  | 144 | 266.1 |
| 7 | 6 | 8 | 8 |  | 8 | 7 |  | 7 | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 8 |  | 8 |  | 8 |  | TSW |  | TSW | 8 | 7 |  | 146 | 269.5 |
| 7 | 6 | 8 | 8 |  | 8 | 8 |  | 7 | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 8 |  | 8 |  | 8 |  | 8 |  | TSW |  | TSW | 8 | 7 |  | 148 | 272.9 |
| 7 | 6 | 8 | 8 |  | 8 | 8 |  | 8 | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | TSW |  | TSW | 8 | 7 |  | 150 | 276.3 |
| 7 | 6 | 8 | 8 |  | 8 | 8 |  | 8 | 8 | 7 | 7 |  | 7 |  | 7 | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | TSW |  | TSW | 8 | 7 |  | 152 | 279.7 |
| 7 | 6 | 8 | 8 |  | 8 | 8 |  | 8 | 8 | 8 | 7 |  | 7 |  | 8 | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | TSW |  | TSW | 8 | 7 |  | 154 | 283.1 |
| 7 | 6 | 8 | 8 |  | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | TSW |  | TSW | 8 | 7 |  | 156 | 286.5 |
| 8 | 6 | 8 | 8 |  | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | TSW |  | TSW | 8 | 8 |  | 158 | 289.9 |
| 8 | 6 | 8 | 8 |  | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 160 | 293.1 |
| 8 | 6 | 9 | 8 |  | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 |  | 8 |  | 9 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 162 | 296.3 |
| 8 | 6 | 9 | 9 |  | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 |  | 9 |  | 9 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 164 | 299.5 |
| 8 | 6 | 9 | 9 |  | 9 | 8 |  | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 9 |  | 9 |  | 9 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 166 | 302.7 |
| 8 | 6 | 9 | 9 |  | 9 | 9 |  | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 168 | 305.9 |
| 8 | 6 | 9 | 9 |  | 9 | 9 |  | 9 | 8 | 8 | 8 |  | 8 |  | 8 | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 170 | 309.1 |
| 8 | 6 | 9 | 9 |  | 9 | 9 |  | 9 | 9 | 8 | 8 |  | 8 |  | 9 | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 172 | 312.3 |
| 8 | 6 | 9 | 9 |  | 9 | 9 |  | 9 | 9 | 9 | 8 |  | 9 |  | 9 | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 174 | 315.5 |
| 9 | 6 | 9 | 9 |  | 9 | 9 |  | 9 | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | TSW |  | TSW | 9 | 8 |  | 176 | 318.7 |
| 9 | 6 | 9 | 9 |  | 9 | 9 |  | 9 | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 10 |  | TSW |  | TSW | 9 | 9 |  | 178 | 321.9 |
| 9 | 6 | 10 | 9 |  | 9 | 9 |  | 9 | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 10 |  | TSW |  | TSW | 10 | 9 |  | 180 | 325.1 |
| 9 | 6 | 10 | 10 |  | 9 | 9 |  | 9 | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 |  | 9 |  | 10 |  | 10 |  | TSW |  | TSW | 10 | 9 |  | 182 | 328.3 |
| 9 | 6 | 10 | 10 |  | 10 | 9 |  | 9 | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 |  | 10 |  | 10 |  | 10 |  | TSW |  | TSW | 10 | 9 |  | 184 | 331.5 |
| 9 | 6 | 10 | 10 |  | 10 | 10 |  | 9 | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 10 |  | 10 |  | 10 |  | 10 |  | TSW |  | TSW | 10 | 9 |  | 186 | 334.7 |
| 9 | 6 | 10 | 10 |  | 10 | 10 |  | 10 | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | TSW |  | TSW | 10 | 9 |  | 188 | 337.9 |
| 9 | 6 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 9 | 9 |  | 9 |  | 9 | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | TSW |  | TSW | 10 | 9 |  | 190 | 341.1 |
| 9 | 6 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 9 |  | 9 |  | 10 | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | TSW |  | TSW | 10 | 9 |  | 192 | 344.3 |
| 9 | 6 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | TSW |  | TSW | 10 | 9 |  | 194 | 347.5 |
| 10 | 6 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | TSW |  | TSW | 10 | 10 |  | 196 | 350.7 |
| 10 | 6 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 198 | 353.7 |
| 10 | 6 | 11 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 |  | 10 |  | 11 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 200 | 356.7 |
| 10 | 6 | 11 | 11 |  | 10 | 10 |  | 10 | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 |  | 11 |  | 11 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 202 | 359.7 |
| 10 | 6 | 11 | 11 |  | 11 | 10 |  | 10 | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 11 |  | 11 |  | 11 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 204 | 362.7 |
| 10 | 6 | 11 | 11 |  | 11 | 11 |  | 10 | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 206 | 365.7 |
| 10 | 6 | 11 | 11 |  | 11 | 11 |  | 11 | 10 | 10 | 10 |  | 10 |  | 10 | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 208 | 368.7 |
| 10 | 6 | 11 | 11 |  | 11 | 11 |  | 11 | 11 | 10 | 10 |  | 10 |  | 11 | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 210 | 371.7 |
| 10 | 6 | 11 | 11 |  | 11 | 11 |  | 11 | 11 | 11 | 10 |  | 11 |  | 11 | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 212 | 374.7 |
| 11 | 6 | 11 | 11 |  | 11 | 11 |  | 11 | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | TSW |  | TSW | 11 | 10 |  | 214 | 377.7 |
| 11 | 6 | 11 | 11 |  | 11 | 11 |  | 11 | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 12 |  | TSW |  | TSW | 11 | 11 |  | 216 | 380.8 |
| 11 | 6 | 12 | 11 |  | 11 | 11 |  | 11 | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 |  | 11 |  | 11 |  | 12 |  | TSW |  | TSW | 12 | 11 |  | 218 | 384 |
| 11 | 6 | 12 | 12 |  | 11 | 11 |  | 11 | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 |  | 11 |  | 12 |  | 12 |  | TSW |  | TSW | 12 | 11 |  | 220 | 387.2 |
| 11 | 6 | 12 | 12 |  | 12 | 11 |  | 11 | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 |  | 12 |  | 12 |  | 12 |  | TSW |  | TSW | 12 | 11 |  | 222 | 390.4 |
| 11 | 6 | 12 | 12 |  | 12 | 12 |  | 11 | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 12 |  | 12 |  | 12 |  | 12 |  | TSW |  | TSW | 12 | 11 |  | 224 | 393.6 |
| 11 | 6 | 12 | 12 |  | 12 | 12 |  | 12 | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | TSW |  | TSW | 12 | 11 |  | 226 | 396.8 |
| 11 | 6 | 12 | 12 |  | 12 | 12 |  | 12 | 12 | 11 | 11 |  | 11 |  | 11 | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | TSW |  | TSW | 12 | 11 |  | 228 | 400 |
| 11 | 6 | 12 | 12 |  | 12 | 12 |  | 12 | 12 | 12 | 11 |  | 11 |  | 12 | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | TSW |  | TSW | 12 | 11 |  | 230 | 403.2 |
| 11 | 6 | 12 | 12 |  | 12 | 12 |  | 12 | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | TSW |  | TSW | 12 | 11 |  | 232 | 406.4 |
| 12 | 6 | 12 | 12 |  | 12 | 12 |  | 12 | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | TSW |  | TSW | 12 | 12 |  | 234 | 409.6 |
| 12 | 6 | 12 | 12 |  | 12 | 12 |  | 12 | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 13 |  | TSW |  | TSW | 13 | 12 |  | 236 | 412.8 |
| 12 | 6 | 13 | 12 |  | 12 | 12 |  | 12 | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 |  | 12 |  | 13 |  | 13 |  | TSW |  | TSW | 13 | 12 |  | 238 | 416 |

Table MCN-9. [pg 1 of 5]. McNary Dam Spill Patterns with No TSWs and Bays 2 and 19 Locked at 4 or 6 Stops.

| MCN Spill Patterns with NO TSWs (# Gate Stops per Spillbay) and Bays 2, 19 Locked at 4 or 6 Stops (in effect until crane repairs are completed) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total Stops | Spill a |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 b | 2 | 3 | 4 | 5 |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 16 | 17 | 18 | 19 | 20 | 21 | 22 b | (#) | (kcfs) |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 |  |  |  | 4 | 7.2 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 | 4 |  |  |  | 5 | 9.2 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 | 4 |  |  |  | 6 | 11.1 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 | 4 | 1 |  |  | 7 | 13.1 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 | 4 | 2 |  |  | 8 | 15.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  | 2 | 4 | 2 |  |  | 9 | 17.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 |  |  |  | 2 | 4 | 2 |  |  | 10 | 18.9 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 | 2 |  |  |  | 2 | 4 | 2 |  |  | 11 | 20.9 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 12 | 22.8 |
|  |  |  |  |  |  |  |  |  |  |  |  | 1 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 13 | 24.8 |
|  |  |  |  |  |  |  |  |  |  |  |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 14 | 26.7 |
|  |  |  |  |  |  |  |  |  |  | 1 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 15 | 28.7 |
|  |  |  |  |  |  |  |  |  |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 16 | 30.6 |
|  |  |  |  |  |  |  |  | 1 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 17 | 32.6 |
|  |  |  |  |  |  |  |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 18 | 34.5 |
|  |  |  |  |  |  | 1 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 19 | 36.5 |
|  |  |  |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 20 | 38.4 |
|  |  | 1 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 21 | 40.4 |
|  |  | 2 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 22 | 42.3 |
|  |  | 3 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 23 | 44.0 |
| 1 |  | 3 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 24 | 46.0 |
| 2 |  | 3 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 25 | 47.9 |
| 3 |  | 3 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  |  | 2 | 4 | 2 |  |  | 26 | 49.6 |
| 3 |  | 3 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 1 | 2 | 4 | 2 |  |  | 27 | 51.6 |
| 3 |  | 3 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 2 | 4 | 2 |  |  | 28 | 53.5 |
| 3 |  | 3 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 3 | 4 | 2 |  |  | 29 | 55.2 |
| 3 |  | 3 |  |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 30 | 56.8 |
| 3 |  | 3 | 1 |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 31 | 58.8 |
| 3 |  | 3 | 2 |  |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 32 | 60.7 |
| 3 |  | 3 | 2 | 1 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 33 | 62.7 |
| 3 |  | 3 | 2 | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 34 | 64.6 |
| 3 |  | 3 | 2 | 2 |  | 2 | 1 | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 35 | 66.6 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 |  | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 36 | 68.5 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 | 1 | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 37 | 70.5 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 38 | 72.4 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 |  | 2 | 1 | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 39 | 74.4 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 |  |  | 2 | 4 | 4 | 2 |  |  | 40 | 76.3 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 1 | 2 | 4 | 4 | 2 |  |  | 41 | 78.3 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 42 | 80.2 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 43 | 82.2 |
| 3 |  | 3 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 44 | 84.1 |
| 3 |  | 4 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 45 | 85.7 |
| 3 |  | 5 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 46 | 87.3 |
| 3 |  | 5 | 3 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 47 | 89.0 |
| 3 |  | 5 | 3 | 2 |  | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 48 | 90.7 |
| 3 |  | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 49 | 92.4 |
| 3 |  | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 50 | 94.1 |
| 3 |  | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 2 |  | 2 | 2 | 4 | 4 | 2 |  |  | 51 | 95.8 |
| 3 |  | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 2 | 4 | 4 | 2 |  |  | 52 | 97.5 |
| 3 |  | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 |  |  | 53 | 99.2 |
| 3 |  | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 1 |  | 54 | 101.2 |
| 3 |  | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 2 |  | 55 | 103.1 |
| 3 | 4 | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 2 | 4 | 4 | 2 |  |  | 56 | 104.7 |
| 3 | 4 | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 |  |  | 57 | 106.4 |
| 3 | 4 | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 1 |  | 58 | 108.4 |
| 3 | 4 | 5 | 3 | 2 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 2 |  | 59 | 110.3 |
| 3 | 4 | 5 | 3 | 3 |  | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 2 |  | 60 | 112.0 |
| 3 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 2 |  | 61 | 113.7 |
| 3 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 2 | 1 | 62 | 115.7 |
| 3 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 2 | 2 | 63 | 117.6 |
| 3 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 3 | 2 | 64 | 119.3 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 3 | 2 | 65 | 120.9 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 3 | 2 | 66 | 122.6 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 3 | 2 | 67 | 124.3 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 3 |  | 2 | 3 | 4 | 4 | 2 | 3 | 2 | 68 | 126.0 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 2 | 3 | 4 | 4 | 2 | 3 | 2 | 69 | 127.7 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 4 | 4 | 2 | 3 | 2 | 70 | 129.4 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 4 | 4 | 3 | 3 | 2 | 71 | 131.1 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 4 | 4 | 3 | 3 | 3 | 72 | 132.8 |
| 4 | 4 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 4 | 4 | 4 | 3 | 3 | 73 | 134.4 |
| 4 | 4 | 5 | 3 | 4 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 4 | 4 | 4 | 3 | 3 | 74 | 136.0 |
| 4 | 4 | 5 | 3 | 4 |  | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 4 | 4 | 4 | 3 | 3 | 75 | 137.6 |
| 4 | 4 | 5 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 4 | 4 | 4 | 3 | 3 | 76 | 139.2 |
| 4 | 4 | 5 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 3 | 3 | 3 |  | 3 | 3 | 4 | 4 | 4 | 3 | 3 | 77 | 140.8 |
| 4 | 4 | 5 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 3 |  | 3 | 3 | 4 | 4 | 4 | 3 | 3 | 78 | 142.4 |
| 4 | 4 | 5 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 |  | 3 | 3 | 4 | 4 | 4 | 3 | 3 | 79 | 144.0 |
| 4 | 4 | 5 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 |  | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 80 | 145.6 |
| 4 | 4 | 5 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 |  | 3 | 4 | 4 | 4 | 5 | 3 | 3 | 81 | 147.2 |
| 4 | 4 | 6 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 |  | 3 | 4 | 4 | 4 | 5 | 3 | 3 | 82 | 148.8 |
| 4 | 4 | 6 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 |  | 3 | 4 | 4 | 4 | 5 | 3 | 4 | 83 | 150.4 |
| 4 | 4 | 6 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 |  | 3 | 4 | 4 | 4 | 5 | 4 | 4 | 84 | 152.0 |
| 4 | 4 | 6 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 85 | 153.6 |
| 4 | 4 | 6 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 86 | 155.2 |
| 4 | 4 | 6 | 3 | 4 |  | 3 | 4 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 87 | 156.8 |
| 4 | 4 | 6 | 3 | 4 |  | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 88 | 158.4 |
| 4 | 4 | 6 | 3 | 4 |  | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 89 | 160.0 |
| 4 | 4 | 6 | 3 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 90 | 161.6 |
| 4 | 4 | 6 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 91 | 163.2 |
| 5 | 4 | 6 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 92 | 164.8 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 93 | 166.4 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 94 | 168.0 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 95 | 169.6 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 96 | 171.2 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 4 |  | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 97 | 172.8 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 4 |  | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 98 | 174.4 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 |  | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 99 | 176.0 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 |  | 4 | 5 | 5 | 4 | 5 | 4 | 4 | 100 | 177.6 |
| 5 | 4 | 6 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 |  | 4 | 5 | 5 | 4 | 6 | 4 | 4 | 101 | 179.2 |
| 5 | 4 | 7 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 |  | 4 | 5 | 5 | 4 | 6 | 4 | 4 | 102 | 180.8 |
| 5 | 4 | 7 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 |  | 4 | 5 | 5 | 4 | 6 | 4 | 5 | 103 | 182.4 |
| 5 | 4 | 7 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 |  | 4 | 5 | 5 | 4 | 6 | 5 | 5 | 104 | 184.0 |
| 5 | 4 | 7 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 105 | 185.6 |
| 5 | 4 | 7 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 5 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 106 | 187.2 |
| 5 | 4 | 7 | 4 | 5 |  | 4 | 5 | 4 | 5 | 4 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 107 | 188.8 |
| 5 | 4 | 7 | 4 | 5 |  | 4 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 108 | 190.4 |
| 5 | 4 | 7 | 4 | 5 |  | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 109 | 192.0 |
| 5 | 4 | 7 | 4 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 110 | 193.6 |
| 5 | 4 | 7 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 111 | 195.2 |
| 6 | 4 | 7 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 112 | 196.8 |
| 6 | 4 | 7 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 4 | 6 | 5 | 5 | 113 | 198.4 |
| 6 | 6 | 7 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 114 | 200.0 |
| 6 | 6 | 7 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 4 | 6 | 5 | 5 | 115 | 201.6 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 4 | 6 | 5 | 5 | 116 | 203.2 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 4 | 6 | 5 | 5 | 117 | 204.8 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 4 | 6 | 5 | 5 | 118 | 206.4 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 6 | 6 | 5 | 5 | 119 | 208.0 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 6 | 6 | 5 | 5 | 120 | 209.6 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 6 | 6 | 5 | 5 | 121 | 211.2 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 5 |  | 5 | 5 | 6 | 6 | 6 | 5 | 5 | 122 | 212.8 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 |  | 5 | 5 | 6 | 6 | 6 | 5 | 5 | 123 | 214.4 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 |  | 5 | 6 | 6 | 6 | 6 | 5 | 5 | 124 | 216.0 |
| 6 | 6 | 7 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 |  | 5 | 6 | 6 | 6 | 7 | 5 | 5 | 125 | 217.6 |
| 6 | 6 | 8 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 |  | 5 | 6 | 6 | 6 | 7 | 5 | 5 | 126 | 219.3 |
| 6 | 6 | 8 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 |  | 5 | 6 | 6 | 6 | 7 | 5 | 6 | 127 | 220.9 |
| 6 | 6 | 8 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 |  | 5 | 6 | 6 | 6 | 7 | 6 | 6 | 128 | 222.5 |
| 6 | 6 | 8 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 129 | 224.1 |
| 6 | 6 | 8 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 130 | 225.7 |
| 6 | 6 | 8 | 5 | 6 |  | 5 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 131 | 227.3 |
| 6 | 6 | 8 | 5 | 6 |  | 5 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 132 | 228.9 |
| 6 | 6 | 8 | 5 | 6 |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 133 | 230.5 |
| 6 | 6 | 8 | 5 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 134 | 232.1 |
| 6 | 6 | 8 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 135 | 233.7 |
| 7 | 6 | 8 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 136 | 235.3 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 137 | 236.9 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 7 | 6 | 7 | 6 | 6 | 138 | 238.5 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 7 | 6 | 7 | 6 | 6 | 139 | 240.1 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 7 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 7 | 6 | 7 | 6 | 6 | 140 | 241.7 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 6 | 6 | 6 |  | 6 | 6 | 7 | 6 | 7 | 6 | 6 | 141 | 243.3 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 6 |  | 6 | 6 | 7 | 6 | 7 | 6 | 6 | 142 | 244.9 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 |  | 6 | 6 | 7 | 6 | 7 | 6 | 6 | 143 | 246.5 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 |  | 6 | 7 | 7 | 6 | 7 | 6 | 6 | 144 | 248.1 |
| 7 | 6 | 8 | 6 | 7 |  | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 |  | 6 | 7 | 7 | 6 | 8 | 6 | 6 | 145 | 249.8 |
| 7 | 6 | 9 | 6 | 7 |  | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 |  | 6 | 7 | 7 | 6 | 8 | 6 | 6 | 146 | 251.4 |
| 7 | 6 | 9 | 6 | 7 |  | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 |  | 6 | 7 | 7 | 6 | 8 | 6 | 7 | 147 | 253.0 |
| 7 | 6 | 9 | 6 | 7 | 6 |  | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 |  | 7 | 7 | 6 | 8 | 7 | 7 | 148 | 254.6 |  |
| 7 | 6 | 9 | 6 | 7 | 6 |  | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 149 | 256.2 |  |
| 7 | 6 | 9 | 6 | 7 | 6 |  | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 7 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 150 | 257.8 |  |
| 7 | 6 | 9 | 6 | 7 | 6 |  | 7 | 6 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 151 | 259.4 |  |
| 7 | 6 | 9 | 6 | 7 | 6 |  | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 152 | 261.0 |  |
| 7 | 6 | 9 | 6 | 7 | 6 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 153 | 262.6 |  |
| 7 | 6 | 9 | 6 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 154 | 264.2 |  |
| 7 | 6 | 9 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 155 | 265.8 |  |
| 8 | 6 | 9 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 156 | 267.5 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 6 | 8 | 7 | 7 | 157 | 269.2 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 8 | 6 | 8 | 7 | 7 | 158 | 270.9 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 8 | 6 | 8 | 7 | 7 | 159 | 272.6 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 8 | 6 | 8 | 7 | 7 | 160 | 274.3 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 7 | 7 | 7 |  | 7 | 8 | 6 | 8 | 7 | 7 | 161 | 276.0 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 7 |  | 7 | 8 | 6 | 8 | 7 | 7 | 162 | 277.7 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 |  | 7 | 8 | 6 | 8 | 7 | 7 | 163 | 279.4 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 |  | 8 | 8 | 6 | 8 | 7 | 7 | 164 | 281.1 |  |
| 8 | 6 | 9 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 |  | 8 | 8 | 6 | 9 | 7 | 7 | 165 | 282.7 |  |
| 8 | 6 | 10 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 |  | 8 | 8 | 6 | 9 | 7 | 7 | 166 | 284.3 |  |
| 8 | 6 | 10 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 |  | 8 | 8 | 6 | 9 | 7 | 8 | 167 | 286.0 |  |
| 8 | 6 | 10 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 |  | 8 | 8 | 6 | 9 | 8 | 8 | 168 | 287.7 |  |
| 8 | 6 | 10 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 169 | 289.4 |  |
| 8 | 6 | 10 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 8 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 170 | 291.1 |  |
| 8 | 6 | 10 | 7 | 8 | 7 |  | 8 | 7 | 8 | 7 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 171 | 292.8 |  |
| 8 | 6 | 10 | 7 | 8 | 7 |  | 8 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 172 | 294.5 |  |
| 8 | 6 | 10 | 7 | 8 | 7 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 173 | 296.2 |  |
| 8 | 6 | 10 | 7 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 174 | 297.9 |  |
| 8 | 6 | 10 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 175 | 299.6 |  |
| 9 | 6 | 10 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 176 | 301.2 |  |
| 9 | 6 | 10 | 8 | 9 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 6 | 9 | 8 | 8 | 177 | 302.8 |  |
| 9 | 6 | 10 | 8 | 9 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 9 | 6 | 9 | 8 | 8 | 178 | 304.4 |  |